## Protocol Explanation
SOFAR Modbus Protocol - G3
valid for these products: | HYD 5 … 20K-3PH and HYD3 … 6K-EP
SOFAR 80 … 136KTL
SOFAR 5 … 24KTL-G3
Version | 1.2 (02.12.2020)
RS485 settings | 9600 bps, 1 starting byte; 8 data bytes; 1 stop byte; Parity: none
Write Format
Device Address | Function Code | Start Address |  | Write Register No. |  | Write Byte No. | Data to write in |  |  |  |  | CRC
1 Byte | 1 Byte | Hi Byte | Low Byte | Hi Byte | Low Byte | 1 Byte | Hi Byte1 | Low Byte1 | … | Hi Byten | Low Byten | Low Byte | Hi Byte
Broadcast Address:0x00; Device Address:1-247 | Write Function Code:0x10 | [5 empty] | For 32bits or 64bit data, it will be sent by Big-endian mode if there is no special explanation. For example, sequence to send a 32bits data: byte3, byte2, byte1, byte0 |  |  |  |  | Modbus-CRC16
Response Format of Write
Device Address | Function Code | Start Address |  | Write Register No. |  | CRC
1 Byte | 1 Byte | Hi Byte | Low Byte | Hi Byte | Low Byte | Low Byte | Hi Byte
Slave Address | Write Function Code:0x10 |  |  |  |  | Modbus-CRC16
Read Format
Device Address | Function Code | Start Address |  | Read Register No. |  | CRC
1 Byte | 1 Byte | Hi Byte | Low Byte | Hi Byte | Low Byte | Low Byte | Hi Byte
Device Address:1-247 | ReadFunction Code:0x03 |  |  |  |  | Modbus-CRC16
Response Format of Read
Device Address | Function Code | Data Byte No. | Response register data |  |  |  |  | CRC
1 Byte | 1 Byte | 1 Byte | Hi Byte1 | Low Byte1 | … | Hi Byte N | Low Byte N | Low Byte | Hi Byte
Slave Address | ReadFunction Code:0x03 |  | For 32bits or 64bit data, it will be sent by Big-endian mode if there is no special explaination. For example , sequence to send a 32bits data: byte3,byte2,byte1,byte0 |  |  |  |  | Modbus-CRC16
Abnormal Response
Device Address | Function Code | Error Code |  | CRC
1 Byte | 1 Byte | 1 Byte |  | Low Byte | Hi Byte
Slave Address | Abnormal Function Code:0x90 | See Error Code List |  | Modbus-CRC16
Error Code List
Value | Explain
1 | illegal function
2 | illegal register address
3 | illegal register value
4 | slave device fault
7 | slave device busy

## Registers
Register address Field Type Accuracy Unit Min. Max. Read and write attributes Remarks Confidentiality level | Register address (Hex) | Field |  | Accuracy | Unit | Min | Max |  | Remarks |  | Mask claculation
Real time data(0x0400-0x07FF)
system info(0x0400-0x047F)
| 0400 | AddressMask_Realtime_SysInfo1 | U64 |  |  |  |  | R | The validity of 64 addresses above the address range (including the address of this partition) corresponding to each bit of this partition. 0 means invalid; 1 means valid. | End user | 0003FFC1 | 0581FFFF
| 0401 | [8 empty] | End user
| 0402 | [8 empty] | End user
| 0403 | [8 empty] | End user
| 0404 | SysState | U16 |  |  |  |  | R | Operating status 0: waiting state 1: Detection status 2: Grid-connected status 3: Emergency power supply status 4: Recoverable fault state 5: Permanent fault status 6: Upgrade status 7: Self-charging status | End user | 1 | 16
| 0405 | Fault1 | U16 |  |  |  |  | R | Fault information table 1 | End user | 1 | 32
| 0406 | Fault2 | U16 |  |  |  |  | R | Fault information table 2 | End user | 1 | 64
| 0407 | Fault3 | U16 |  |  |  |  | R | Fault information table 3 | End user | 1 | 128
| 0408 | Fault4 | U16 |  |  |  |  | R | Fault information table 4 | End user | 1 | 256
| 0409 | Fault5 | U16 |  |  |  |  | R | Fault information table 5 | End user | 1 | 512
| 040A | Fault6 | U16 |  |  |  |  | R | Fault information table 6 | End user | 1 | 1024
| 040B | Fault7 | U16 |  |  |  |  | R | Fault information table 7 | End user | 1 | 2048
| 040C | Fault8 | U16 |  |  |  |  | R | Fault information table 8 | End user | 1 | 4096
| 040D | Fault9 | U16 |  |  |  |  | R | Fault information table 9 | End user | 1 | 8192
| 040E | Fault10 | U16 |  |  |  |  | R | Fault information table 10 | End user | 1 | 16384
| 040F | Fault11 | U16 |  |  |  |  | R | Fault information table 11 | End user | 1 | 32768
| 0410 | Fault12 | U16 |  |  |  |  | R | Fault information table 12 | End user | 1 | 65536
| 0411 | Fault13 | U16 |  |  |  |  | R | Fault information table 13 | End user |  | 0
| 0412 | Fault14 | U16 |  |  |  |  | R | Fault information table 14 | End user |  | 0
| 0413 | Fault15 | U16 |  |  |  |  | R | Fault information table 15 | End user |  | 0
| 0414 | Fault16 | U16 |  |  |  |  | R | Fault information table 16 | End user |  | 0
| 0415 | Fault17 | U16 |  |  |  |  | R | Fault information table 17 | End user |  | 0
| 0416 | Fault18 | U16 |  |  |  |  | R | Fault information table 18 | End user |  | 0
| 0417 | Countdown | U16 | 1 | seconds |  |  | R | Power-on countdown | End user | 1 | 8388608
| 0418 | Temperature_Env1 | I16 | 1 | °C |  |  | R | Ambient temperature 1 | End user | 1 | 16777216
| 0419 | Temperature_Env2 | I16 | 1 | °C |  |  | R | Ambient temperature 2 | End user |  | 0
| 041A | Temperature_HeatSink1 | I16 | 1 | °C |  |  | R | Radiator temperature 1 | End user | 1 | 67108864
| 041B | Temperature_HeatSink2 | I16 | 1 | °C |  |  | R | Radiator temperature 2 | End user |  | 0
| 041C | Temperature_HeatSink3 | I16 | 1 | °C |  |  | R | Radiator temperature 3 | End user |  | 0
| 041D | Temperature_HeatSink4 | I16 | 1 | °C |  |  | R | Radiator temperature 4 | End user |  | 0
| 041E | Temperature_HeatSink5 | I16 | 1 | °C |  |  | R | Radiator temperature 5 | End user |  | 0
| 041F | Temperature_HeatSink6 | I16 | 1 | °C |  |  | R | Radiator temperature 6 | End user |  | 0
| 0420 | Temperature_Inv1 | I16 | 1 | °C |  |  | R | Module temperature 1 | End user | 1 | 4294967296
| 0421 | Temperature_Inv2 | I16 | 1 | °C |  |  | R | Module temperature 2 | End user |  | 0
| 0422 | Temperature_Inv3 | I16 | 1 | °C |  |  | R | Module temperature 3 | End user |  | 0
| 0423 | Temp_Rsvd1 | I16 | 1 | °C |  |  | R | Reserve temperature 1 | End user |  | 0
| 0424 | Temp_Rsvd2 | I16 | 1 | °C |  |  | R | Reserve temperature 2 | End user |  | 0
| 0425 | Temp_Rsvd3 | I16 | 1 | °C |  |  | R | Reserve temperature 3 | End user |  | 0
| 0426 | GenerationTime_Today | U16 | 1 | Minute |  |  | R | Day of power generation time | End user | 1 | 274877906944
| 0427 | GenerationTime_Total | U32 | 1 | Minute |  |  | R | Total power generation time | End user | 1 | 549755813888
| 0428 | [8 empty] | End user | 1 | 1099511627776
| 0429 | ServiceTime_Total | U32 | 1 | Minute |  |  | R | Total running time | End user | 1 | 2199023255552
| 042A | [8 empty] | End user | 1 | 4398046511104
| 042B | InsulationResistance | U16 | 1 | kΩ |  |  | R | Insulation resistance | End user | 1 | 8796093022208
| 042C | SysTime_Year | U16 |  |  |  |  | R | System time-year | End user | 1 | 17592186044416
| 042D | SysTime_Month | U16 |  |  |  |  | R | System time-month | End user | 1 | 35184372088832
| 042E | SysTime_Date | U16 |  |  |  |  | R | System Time-Daily Minutes | End user | 1 | 70368744177664
| 042F | SysTime_Hour | U16 |  |  |  |  | R | System time-hour | End user | 1 | 140737488355328
| 0430 | SysTime_Minute | U16 |  |  |  |  | R | System time-minutes | End user | 1 | 281474976710656
| 0431 | SysTime_Second | U16 |  |  |  |  | R | System time-second | End user | 1 | 562949953421312
| 0432 | Fault19 | U16 |  |  |  |  | R | Fault message table 19 | End user
| 0433 | Fault20 | U16 |  |  |  |  | R | Fault information table 20 | End user
| 0434 | Fault21 | U16 |  |  |  |  | R | Fault information table 21 | End user
| 0435 | Fault22 | U16 |  |  |  |  | R | Fault information table 22 | End user
| 0436 | Fault23 | U16 |  |  |  |  | R | Fault information table 23 | End user
| 0437 | Fault24 | U16 |  |  |  |  | R | Fault message table 24 | End user
| 0438 | Fault25 | U16 |  |  |  |  | R | Fault information table 25 | End user
| 0439 | Fault26 | U16 |  |  |  |  | R | Fault message table 26 | End user
| 043A | Fault27 | U16 |  |  |  |  | R | Fault information table 27 | End user
043B
043C
043D
043E
043F
| 0440 | AddressMask_Realtime_SysInfo2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid | End user | 00000000 | 1FFFEFEF
| 0441 | [8 empty] | End user
| 0442 | [8 empty] | End user
| 0443 | [8 empty] | End user
| 0444 | Production_Code | U16 | [5 empty] | Reverse |  | 0 | 0
| 0445 | Serial_Number0 | ASCII |  |  |  |  | R | The first and second digits of the serial number. The upper 8 bits of the register store the first bit of the serial number; The lower 8 bits of the register store the second bit of the serial number. | End user | 1 | 32
| 0446 | Serial_Number1 | ASCII |  |  |  |  | R | The 3rd and 4th digits of the serial number. The upper 8 bits of the register store the third bit of the serial number; The lower 8 bits of the register store the 4th bit of the serial number. | End user | 1 | 64
| 0447 | Serial_Number2 | ASCII |  |  |  |  | R | The 5th and 6th digits of the serial number. The upper 8 bits of the register store the 5th bit of the serial number; The lower 8 bits of the register store the 6th bit of the serial number. | End user | 1 | 128
| 0448 | Serial_Number3 | ASCII |  |  |  |  | R | The 7th and 8th digits of the serial number. The upper 8 bits of the register store the 7th bit of the serial number; The lower 8 bits of the register store the 8th bit of the serial number. | End user | 1 | 256
| 0449 | Serial_Number4 | ASCII |  |  |  |  | R | The 9th and 10th digits of the serial number. The upper 8 bits of the register store the 9th bit of the serial number; The lower 8 bits of the register store the 10th bit of the serial number. | End user | 1 | 512
| 044A | Serial_Number5 | ASCII |  |  |  |  | R | The 11th and 12th digits of the serial number. The upper 8 bits of the register store the 11th bit of the serial number; The lower 8 bits of the register store the 12th bit of the serial number. | End user | 1 | 1024
| 044B | Serial_Number6 | ASCII |  |  |  |  | R | The 13th and 14th digits of the serial number. The upper 8 bits of the register store the 13th bit of the serial number; The lower 8 bits of the register store the 14th bit of the serial number. | End user | 1 | 2048
| 044C | Serial_Number7 | ASCII |  |  |  |  | R | Reverse
| 044D | Hardware_Version0 | ASCII |  |  |  |  | R | The first and second digits of the hardware version number. The upper 8 bits of the register store the first bit of the serial number; The lower 8 bits of the register store the second bit of the serial number. | End user | 1 | 8192
| 044E | Hardware_Version1 | ASCII |  |  |  |  | R | The third and fourth digits of the hardware version number. The upper 8 bits of the register store the third bit of the serial number; The lower 8 bits of the register store the 4th bit of the serial number. | End user | 1 | 16384
| 044F | Software_Version_Stage_COM | ASCII |  |  |  |  | R | Communication chip software version number stage definition bit. The lower 8 bits of the register store the ASCII code. The default value of the official version is'V'. | End user | 1 | 32768
| 0450 | Software_Version_Major_COM | ASCII |  |  |  |  | R | The main version number of the communication chip software. The major version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The upper 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits | End user | 1 | 65536
| 0451 | Software_Version_Custom_COM | ASCII |  |  |  |  | R | Communication chip software non-standard customized version number. The version number of the standard software is ""00"". The non-standard customized version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The upper 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End user | 1 | 131072
| 0452 | Software_Version_Minor_COM | ASCII |  |  |  |  | R | Communication chip software sub-version number. The upper 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits | End user | 1 | 262144
| 0453 | Software_Version_Stage_Master | ASCII |  |  |  |  | R | The main controller chip software version number stage definition bit. The lower 8 bits of the register store the ASCII code. The default value of the official version is'V'. The upper 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End user | 1 | 524288
| 0454 | Software_Version_Major_Master | ASCII |  |  |  |  | R | Main controller chip software main version number. The major version numbers of all chips in the same system must be the same, otherwise it is regarded as a system failure. The upper 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End user | 1 | 1048576
| 0455 | Software_Version_Custom_Master | ASCII |  |  |  |  | R | The non-standard customized version number of the main controller chip software. The version number of the standard software is ""00"". The non-standard customized version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The upper 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End user | 1 | 2097152
| 0456 | Software_Version_Minor_Master | ASCII |  |  |  |  | R | 主控制器芯片软件子版本号。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | End user | 1 | 4194304
| 0457 | Software_Version_Stage_Slave | ASCII |  |  |  |  | R | 副控制器芯片软件版本号阶段定义位。 寄存器低8位存放ASCII码。正式版本的默认值为'V'。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | End user | 1 | 8388608
| 0458 | Software_Version_Major_Slave | ASCII |  |  |  |  | R | 副控制器芯片软件主版本号。 同一个系统中所有芯片主版本号必须一致，否则视为系统故障。 寄存器高8位存放高位数字； 寄存器低8位存放低位数字。 | End user | 1 | 16777216
| 0459 | Software_Version_Custom_Slave | ASCII |  |  |  |  | R | Sub-controller chip software non-standard customized version number. The version number of the standard software is ""00"". The non-standard customized version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The upper 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End user | 1 | 33554432
| 045A | Software_Version_Minor_Slave | ASCII |  |  |  |  | R | Sub-controller chip software subversion number. The upper 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. | End user | 1 | 67108864
| 045B | Safety_Version_Major | U16 |  |  |  |  | R | Safety code main version number | End user | 1 | 134217728
| 045C | Safety_version_Minor | U16 |  |  |  |  | R | Safety code vice version number | End user | 1 | 268435456
| 045D | Boot_Version_COM | U16 |  |  |  |  | R |  | End user |  | 0
| 045E | Boot_Version_Master | U16 |  |  |  |  | R |  | End user |  | 0
| 045F | Boot_Version_Slave | U16 |  |  |  |  | R |  | End user |  | 0
| 0460 | Safety_Firmware_Version_Stage | ASCII |  |  |  |  | R | Safety regulation certification software version number stage definition bit. The lower 8 bits of the register store the ASCII code. The default value of the official version is'V'. The upper 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. |  |  | 0
| 0461 | Safety_Firmware_Version_Major | ASCII |  |  |  |  | R | The major version number of the safety regulation certification software. The major version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The upper 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. |  |  | 0
| 0462 | Safety_Firmware_Version_Custom | ASCII |  |  |  |  | R | Safety regulation certification software non-standard customized version number. The version number of the standard software is "00". The non-standard customized version numbers of all chips in the same system must be the same, otherwise it will be regarded as a system failure. The upper 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. |  |  | 0
| 0463 | Safety_Firmware_Version_Minor | ASCII |  |  |  |  | R | Safety regulation certification software sub version number. The upper 8 bits of the register store the high digits; The lower 8 bits of the register store the lower digits. |  |  | 0
| 0464 | Safety_Hardware_Version0 | ASCII |  |  |  |  | R | Safety regulation certification hardware version number 1st and 2nd bit. The upper 8 bits of the register store the first bit of the serial number; The lower 8 bits of the register store the second bit of the serial number. |  |  | 0
| 0465 | Safety_Hardware_Version1 | ASCII |  |  |  |  | R | Safety regulation certification hardware version number 3rd and 4th bit. The upper 8 bits of the register store the first bit of the serial number; The lower 8 bits of the register store the second bit of the serial number. |  |  | 0
| 0466 | [10 empty] | 0
| 0467 | [10 empty] | 0
| 0468 | [10 empty] | 0
| 0469 | [10 empty] | 0
| 046A | [10 empty] | 0
| 046B | [10 empty] | 0
| 046C | [10 empty] | 0
| 046D | [10 empty] | 0
| 046E | [10 empty] | 0
| 046F | [10 empty] | 0
| 0470 | Serial_Number8 | ASCII |  |  |  |  | R |  |  |  | 0
| 0471 | Serial_Number9 | ASCII |  |  |  |  | R |  |  |  | 0
| 0472 | Serial_Number11_Rsvd0 | ASCII |  |  |  |  | R |  |  |  | 0
| 0473 | Serial_Number11_Rsvd1 | ASCII |  |  |  |  | R |  |  |  | 0
| 0474 | Serial_Number12_Rsvd2 | ASCII |  |  |  |  | R |  |  |  | 0
| 0475 | Serial_Number13_Rsvd3 | ASCII |  |  |  |  | R |  |  |  | 0
| 0476 | Serial_Number14_Rsvd4 | ASCII |  |  |  |  | R |  |  |  | 0
| 0477 | [10 empty] | 0
| 0478 | [10 empty] | 0
| 0479 | [10 empty] | 0
| 047A | [10 empty] | 0
| 047B | [10 empty] | 0
| 047C | [10 empty] | 0
| 047D | [10 empty] | 0
| 047E | [10 empty] | 0
| 047F | [10 empty] | 0
on grid output(0x0480-0x04FF)
| 0480 | AddressMask_Realtime_GridOutput1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid. | End user | 0000C118 | 2304613F
| 0481 | [8 empty] | End user
| 0482 | [8 empty] | End user
| 0483 | [8 empty] | End user
| 0484 | Frequency_Grid | U16 | 0.01 | Hz |  |  | R | Grid frequency | End user | 1 | 16
| 0485 | ActivePower_Output_Total | I16 | 0.01 | kW |  |  | R | Total active power. Discharge is positive, charge is negative | End user | 1 | 32
| 0486 | ReactivePower_Output_Total | I16 | 0.01 | kW |  |  | R | Total reactive power. The inverter end is positive for leading and negative for lagging | End user |  | 0
| 0487 | ApparentPower_Output_Total | I16 | 0.01 | kW |  |  | R | Total apparent power. Discharge is positive, charge is negative | End user |  | 0
| 0488 | ActivePower_PCC_Total | I16 | 0.01 | kW |  |  | R | Total PCC active power. Selling electricity is positive, buying electricity is negative | End user | 1 | 256
| 0489 | ReactivePower_PCC_Total | I16 | 0.01 | kW |  |  | R | Total PCC reactive power. The inverter end is positive for lead and negative for lag | End user |  | 0
| 048A | ApparentPower_PCC_Total | I16 | 0.01 | kW |  |  | R | Total PCC apparent power. Selling electricity is positive, buying electricity is negative | End user |  | 0
| 048B | GridOutput_Rsvd1 | [5 empty] | R | Grid-connected output reserved 1 | End user |  | 0
| 048C | GridOutput_Rsvd2 | [5 empty] | R | Grid-connected output reserved 2 | End user |  | 0
| 048D | Voltage_Phase_R | U16 | 0.1 | V |  |  | R | R phase grid voltage | End user | 1 | 8192
| 048E | Current_Output_R | U16 | 0.01 | A |  |  | R | R-phase inverter output current | End user | 1 | 16384
| 048F | ActivePower_Output_R | I16 | 0.01 | kW |  |  | R | The R-phase inverter outputs active power. Discharge is positive, charge is negative | End user |  | 0
| 0490 | ReactivePower_Output_R | I16 | 0.01 | kW |  |  | R | The R-phase inverter outputs reactive power. The inverter end is positive for lead and negative for lag | End user |  | 0
| 0491 | PowerFactor_Output_R | I16 | 0.001 | p.u. |  |  | R | R-phase power factor. The inverter end is positive for lead and negative for lag | End user |  | 0
| 0492 | Current_PCC_R | U16 | 0.01 | A |  |  | R | R phase PCC current | End user | 1 | 262144
| 0493 | ActivePower_PCC_R | I16 | 0.01 | kW |  |  | R | R-phase PCC active power | End user |  | 0
| 0494 | ReactivePower_PCC_R | I16 | 0.01 | kW |  |  | R | R-phase PCC reactive power. The inverter end is positive for lead and negative for lag | End user |  | 0
| 0495 | PowerFactor_PCC_R | I16 | 0.001 | p.u. |  |  | R | R-phase PCC power factor. The inverter end is positive for lead and negative for lag | End user |  | 0
| 0496 | R_Rsvd1 | [5 empty] | R | R phase reserved 1 | End user |  | 0
| 0497 | R_Rsvd2 | [5 empty] | R | R phase reserved 2 | End user |  | 0
| 0498 | Voltage_Phase_S | U16 | 0.1 | V |  |  | R | S phase grid voltage | End user | 1 | 16777216
| 0499 | Current_Output_S | U16 | 0.01 | A |  |  | R | S phase inverter output current | End user | 1 | 33554432
| 049A | ActivePower_Output_S | I16 | 0.01 | kW |  |  | R | The S-phase inverter outputs active power. Discharge is positive, charge is negative | End user |  | 0
| 049B | ReactivePower_Output_S | I16 | 0.01 | kW |  |  | R | The S-phase inverter outputs reactive power. The inverter end is positive for lead and negative for lag | End user |  | 0
| 049C | PowerFactor_Output_S | I16 | 0.001 | p.u. |  |  | R | S-phase power factor. The inverter end is positive for lead and negative for lag | End user |  | 0
| 049D | Current_PCC_S | U16 | 0.01 | A |  |  | R | S phase PCC current | End user | 1 | 536870912
| 049E | ActivePower_PCC_S | I16 | 0.01 | kW |  |  | R | S-phase PCC active power. Discharge is positive, charge is negative | End user |  | 0
| 049F | ReactivePower_PCC_S | I16 | 0.01 | kW |  |  | R | S-phase PCC reactive power. The inverter end is positive for lead and negative for lag | End user |  | 0
| 04A0 | PowerFactor_PCC_S | I16 | 0.001 | p.u. |  |  | R | S-phase PCC power factor. The inverter end is positive for lead and negative for lag | End user |  | 0
| 04A1 | S_Rsvd1 | [5 empty] | R | S phase reserved 1 | End user |  | 0
| 04A2 | S_Rsvd2 | [5 empty] | R | S phase reserved 2 | End user |  | 0
| 04A3 | Voltage_Phase_T | U16 | 0.1 | V |  |  | R | T phase grid voltage | End user | 1 | 34359738368
| 04A4 | Current_Output_T | U16 | 0.01 | A |  |  | R | T-phase inverter output current | End user | 1 | 68719476736
| 04A5 | ActivePower_Output_T | I16 | 0.01 | kW |  |  | R | The T-phase inverter outputs active power. Discharge is positive, charge is negative | End user |  | 0
| 04A6 | ReactivePower_Output_T | I16 | 0.01 | kW |  |  | R | The T-phase inverter outputs reactive power. The inverter end is positive for lead and negative for lag | End user |  | 0
| 04A7 | PowerFactor_Output_T | I16 | 0.001 | p.u. |  |  | R | T-phase power factor. The inverter end is positive for lead and negative for lag | End user |  | 0
| 04A8 | Current_PCC_T | U16 | 0.01 | A |  |  | R | T phase PCC current | End user | 1 | 1099511627776
| 04A9 | ActivePower_PCC_T | I16 | 0.01 | kW |  |  | R | T-phase PCC active power. Discharge is positive, charge is negative | End user |  | 0
| 04AA | ReactivePower_PCC_T | I16 | 0.01 | kW |  |  | R | T-phase PCC reactive power. The inverter end is positive for lead and negative for lag | End user |  | 0
| 04AB | PowerFactor_PCC_T | I16 | 0.001 | p.u. |  |  | R | T-phase PCC power factor. The inverter end is positive for lead and negative for lag | End user |  | 0
| 04AC | T_Rsvd1 | [5 empty] | R | T phase reserved 1 | End user |  | 0
| 04AD | T_Rsvd2 | [5 empty] | R | T phase reserved 2 | End user |  | 0
| 04AE | ActivePower_PV_Ext | U16 | 0.01 | kW |  |  | R | External power generation | End user | 1 | 70368744177664
| 04AF | ActivePower_Load_Sys | U16 | 0.01 | kW |  |  | R | System total load power | End user | 1 | 140737488355328
| 04B0 | Voltage_Phase_L1N | U16 | 0.1 | V |  |  | R | Grid L1 to N voltage effective value | End user |  | 0
| 04B1 | Current_Output_L1N | U16 | 0.01 | A |  |  | R | L1 output current effective value | End user |  | 0
| 04B2 | ActivePower_Output_L1N | I16 | 0.01 | kW |  |  | R | Active power output on L1 line | End user |  | 0
i | 04B3 | Current_PCC_L1N | U16 | 0.01 | A |  |  | R | Effective value of CT current on L1 line | End user |  | 0
| 04B4 | ActivePower_PCC_L1N | I16 | 0.01 | kW |  |  | R | PCC active power on L1 line | End user |  | 0
| 04B5 | Voltage_Phase_L2N | U16 | 0.1 | V |  |  | R | Grid L2 to N voltage effective value | End user |  | 0
| 04B6 | Current_Output_L2N | U16 | 0.01 | A |  |  | R | L2 output current effective value | End user |  | 0
| 04B7 | ActivePower_Output_L2N | I16 | 0.01 | kW |  |  | R | Active power output on L2 line | End user |  | 0
| 04B8 | Current_PCC_L2N | U16 | 0.01 | A |  |  | R | Effective value of CT current on L2 line | End user |  | 0
| 04B9 | ActivePower_PCC_L2N | I16 | 0.01 | kW |  |  | R | Active power output on L2 line | End user |  | 0
| 04BA | Voltage_Line_L1 | U16 | 0.1 | V |  |  | R | L1 line voltage: voltage between R/S phase | End user
| 04BB | Voltage_Line_L2 | U16 | 0.1 | V |  |  | R | L2 line voltage: voltage between S/T phase | End user
| 04BC | Voltage_Line_L3 | U16 | 0.1 | V |  |  | R | L3 line voltage: voltage between T/R phase | End user
04BD
04BE
04BF
off grid output(0x0500-0x057F)
| 0500 | AddressMask_Realtime_EmergencyOutput1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid | End user | 00000000 | 1C1C1C9F
| 0501 | [8 empty] | End user
| 0502 | [8 empty] | End user
| 0503 | [8 empty] | End user
| 0504 | ActivePower_Load_Total | I16 | 0.01 | kW |  |  | R | Load active power. | End user | 1 | 16
| 0505 | ReactivePower_Load_Total | I16 | 0.01 | kW |  |  | R | Load consumption is positive, and feedback is negative | End user |  | 0
| 0506 | ApparentPower_Load_Total | I16 | 0.01 | kW |  |  | R | Load reactive power Apparent power of the load. Load consumption is positive, and feedback is negative | End user |  | 0
| 0507 | Frequency_Output | U16 | 0.01 | Hz |  |  | R | Output voltage frequency | End user | 1 | 128
| 0508 | ESOutput_Rsvd1 | [5 empty] | R | Off-grid total output reserved 1 | End user |  | 0
| 0509 | ESOutput_Rsvd2 | [5 empty] | R | Off-grid total output reserved 2 | End user |  | 0
| 050A | Voltage_Output_R | U16 | 0.1 | V |  |  | R | R-phase inverter output voltage | End user | 1 | 1024
| 050B | Current_Load_R | I16 | 0.01 | A |  |  | R | R phase load current | End user | 1 | 2048
| 050C | ActivePower_Load_R | I16 | 0.01 | kW |  |  | R | R-phase load active power. Load consumption is positive, and feedback is negative. | End user | 1 | 4096
| 050D | ReactivePower_Load_R | I16 | 0.01 | kW |  |  | R | R-phase load reactive power. The inverter end is positive for lead and negative for lag | End user |  | 0
| 050E | ApparentPower_Load_R | I16 | 0.01 | kVA |  |  | R | Apparent power of R-phase load. Load consumption is positive, and feedback is negative. | End user |  | 0
| 050F | LoadPeakRatio_R | U16 | 0.01 | p.u. |  |  | R | R phase load peak ratio | End user |  | 0
| 0510 | ESR_Rsvd1 | [5 empty] | R | R phase reserved 1 | End user |  | 0
| 0511 | ESR_Rsvd2 | [5 empty] | R | R phase reserved 2 | End user |  | 0
| 0512 | Voltage_Output_S | U16 | 0.1 | V |  |  | R | S phase inverter output voltage | End user | 1 | 262144
| 0513 | Current_Load_S | I16 | 0.01 | A |  |  | R | S phase load current | End user | 1 | 524288
| 0514 | ActivePower_Load_S | I16 | 0.01 | kW |  |  | R | S-phase load active power. Load consumption is positive, and feedback is negative. | End user | 1 | 1048576
| 0515 | ReactivePower_Load_S | I16 | 0.01 | kW |  |  | R | S-phase load reactive power. The inverter end is positive for lead and negative for lag | End user |  | 0
| 0516 | ApparentPower_Load_S | I16 | 0.01 | kVA |  |  | R | Apparent power of S-phase load. Load consumption is positive, and feedback is negative. | End user |  | 0
| 0517 | LoadPeakRatio_S | U16 | 0.01 | p.u. |  |  | R | S phase load peak ratio | End user |  | 0
| 0518 | ESS_Rsvd1 | [5 empty] | R | S phase reserved 1 | End user |  | 0
| 0519 | ESS_Rsvd2 | [5 empty] | R | S phase reserved 2 | End user |  | 0
| 051A | Voltage_Output_T | U16 | 0.1 | V |  |  | R | T-phase inverter output voltage | End user | 1 | 67108864
| 051B | Current_Load_T | I16 | 0.01 | A |  |  | R | T phase load current | End user | 1 | 134217728
| 051C | ActivePower_Load_T | I16 | 0.01 | kW |  |  | R | T-phase load active power. Load consumption is positive, and feedback is negative. | End user | 1 | 268435456
| 051D | ReactivePower_Load_T | I16 | 0.01 | kW |  |  | R | T-phase load reactive power. The inverter end is positive for lead and negative for lag | End user |  | 0
| 051E | ApparentPower_Load_T | I16 | 0.01 | kVA |  |  | R | Apparent power of T-phase load. Load consumption is positive, and feedback is negative. | End user |  | 0
| 051F | LoadPeakRatio_T | U16 | 0.01 | p.u. |  |  | R | T-phase load peak ratio | End user |  | 0
| 0520 | EST_Rsvd1 | [5 empty] | R | T phase reserved 1 | End user |  | 0
| 0521 | EST_Rsvd2 | [5 empty] | R | T phase reserved 2 | End user |  | 0
| 0522 | Voltage_Output_L1N | U16 | 0.1 | V |  |  | R | Inverter L1 to N voltage effective value | End user |  | 0
| 0523 | Current_Load_L1N | I16 | 0.01 | A |  |  | R | L1 load current effective value | End user |  | 0
| 0524 | ActivePower_Load_L1N | I16 | 0.01 | kW |  |  | R | Load L1 to N active power | End user |  | 0
| 0525 | Voltage_Output_L2N | U16 | 0.1 | V |  |  | R | Effective value of inverter L2 to N voltage | End user |  | 0
| 0526 | Current_Load_L2N | I16 | 0.01 | A |  |  | R | L2 load current effective value | End user |  | 0
| 0527 | ActivePower_Load_L2N | I16 | 0.01 | kW |  |  | R | Load L2 to N active power | End user |  | 0
0528
0529
052A
052B
052C
052D
052E
052F
0530
0531
0532
0533
0534
0535
0536
0537
0538
0539
053A
053B
053C
053D
053E
053F
PV input(0x0580-0x05FF)
| 0580 | AddressMask_Realtime_Input_PV1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | End user | 00000000 | 000003FF
| 0581 | [8 empty] | End user
| 0582 | [8 empty] | End user
| 0583 | [8 empty] | End user
| 0584 | Voltage_PV1 | U16 | 0.1 | V |  |  | R | The first PV voltage | End user | 1 | 16
| 0585 | Current_PV1 | U16 | 0.01 | A |  |  | R | The first PV current | End user | 1 | 32
| 0586 | Power_PV1 | U16 | 0.01 | kW |  |  | R | PV power of the first road | End user | 1 | 64
| 0587 | Voltage_PV2 | U16 | 0.1 | V |  |  | R | The second PV voltage | End user | 1 | 128
| 0588 | Current_PV2 | U16 | 0.01 | A |  |  | R | The second PV current | End user | 1 | 256
| 0589 | Power_PV2 | U16 | 0.01 | kW |  |  | R | PV power of the 2nd road | End user | 1 | 512
| 058A | Voltage_PV3 | U16 | 0.1 | V |  |  | R | No. 3 PV voltage | End user |  | 0
| 058B | Current_PV3 | U16 | 0.01 | A |  |  | R | No. 3 PV current | End user |  | 0
| 058C | Power_PV3 | U16 | 0.01 | kW |  |  | R | No. 3 PV power | End user |  | 0
| 058D | Voltage_PV4 | U16 | 0.1 | V |  |  | R | No. 4 PV voltage | End user |  | 0
| 058E | Current_PV4 | U16 | 0.01 | A |  |  | R | No. 4 PV current | End user |  | 0
| 058F | Power_PV4 | U16 | 0.01 | kW |  |  | R | No. 4 PV power | End user |  | 0
| 0590 | Voltage_PV5 | U16 | 0.1 | V |  |  | R | No. 5 PV voltage | End user |  | 0
| 0591 | Current_PV5 | U16 | 0.01 | A |  |  | R | No. 5 PV current | End user |  | 0
| 0592 | Power_PV5 | U16 | 0.01 | kW |  |  | R | No. 5 PV power | End user |  | 0
| 0593 | Voltage_PV6 | U16 | 0.1 | V |  |  | R | No. 6 PV voltage | End user |  | 0
| 0594 | Current_PV6 | U16 | 0.01 | A |  |  | R | No. 6 PV current | End user |  | 0
| 0595 | Power_PV6 | U16 | 0.01 | kW |  |  | R | No. 6 PV power | End user |  | 0
| 0596 | Voltage_PV7 | U16 | 0.1 | V |  |  | R | No. 7 PV voltage | End user |  | 0
| 0597 | Current_PV7 | U16 | 0.01 | A |  |  | R | No. 7 PV current | End user |  | 0
| 0598 | Power_PV7 | U16 | 0.01 | kW |  |  | R | No. 7 PV power | End user |  | 0
| 0599 | Voltage_PV8 | U16 | 0.1 | V |  |  | R | No. 8 PV voltage | End user |  | 0
| 059A | Current_PV8 | U16 | 0.01 | A |  |  | R | No. 8 PV current | End user |  | 0
| 059B | Power_PV8 | U16 | 0.01 | kW |  |  | R | No. 8 PV power | End user |  | 0
| 059C | Voltage_PV9 | U16 | 0.1 | V |  |  | R | No. 9 PV voltage | End user |  | 0
| 059D | Current_PV9 | U16 | 0.01 | A |  |  | R | No. 9 PV current | End user |  | 0
| 059E | Power_PV9 | U16 | 0.01 | kW |  |  | R | No. 9 PV power | End user |  | 0
| 059F | Voltage_PV10 | U16 | 0.1 | V |  |  | R | No. 10 PV voltage | End user |  | 0
| 05A0 | Current_PV10 | U16 | 0.01 | A |  |  | R | No. 10 PV current | End user |  | 0
| 05A1 | Power_PV10 | U16 | 0.01 | kW |  |  | R | No. 10 PV power | End user |  | 0
| 05A2 | Voltage_PV11 | U16 | 0.1 | V |  |  | R | 11th PV voltage | End user |  | 0
| 05A3 | Current_PV11 | U16 | 0.01 | A |  |  | R | 11th PV current | End user |  | 0
| 05A4 | Power_PV11 | U16 | 0.01 | kW |  |  | R | 11th PV power | End user |  | 0
| 05A5 | Voltage_PV12 | U16 | 0.1 | V |  |  | R | 12th PV voltage | End user |  | 0
| 05A6 | Current_PV12 | U16 | 0.01 | A |  |  | R | 12th PV current | End user |  | 0
| 05A7 | Power_PV12 | U16 | 0.01 | kW |  |  | R | 12th PV power | End user |  | 0
| 05A8 | Voltage_PV13 | U16 | 0.1 | V |  |  | R | 13th PV voltage | End user |  | 0
| 05A9 | Current_PV13 | U16 | 0.01 | A |  |  | R | 13th PV current | End user |  | 0
| 05AA | Power_PV13 | U16 | 0.01 | kW |  |  | R | 13th PV power | End user |  | 0
| 05AB | Voltage_PV14 | U16 | 0.1 | V |  |  | R | No. 14 PV voltage | End user |  | 0
| 05AC | Current_PV14 | U16 | 0.01 | A |  |  | R | No. 14 PV current | End user |  | 0
| 05AD | Power_PV14 | U16 | 0.01 | kW |  |  | R | No. 14 PV power | End user |  | 0
| 05AE | Voltage_PV15 | U16 | 0.1 | V |  |  | R | 15th PV voltage | End user |  | 0
| 05AF | Current_PV15 | U16 | 0.01 | A |  |  | R | 15th PV current | End user |  | 0
| 05B0 | Power_PV15 | U16 | 0.01 | kW |  |  | R | 15th PV power | End user |  | 0
| 05B1 | Voltage_PV16 | U16 | 0.1 | V |  |  | R | 16th PV voltage | End user |  | 0
| 05B2 | Current_PV16 | U16 | 0.01 | A |  |  | R | 16th PV current | End user |  | 0
| 05B3 | Power_PV16 | U16 | 0.01 | kW |  |  | R | 16th PV power | End user |  | 0
05B4
05B5
05B6
05B7
05B8
05B9
05BA
05BB
05BC
05BD
05BE
05BF
| 05C0 | AddressMask_Realtime_Input_PV2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid. | End user | 00000000 | 0000000F
| 05C1 | [8 empty] | End user
| 05C2 | [8 empty] | End user
| 05C3 | [8 empty] | End user
| 05C4 | Power_PV_Total | U16 | 0.1 | kW |  |  | R | Total PV power |  |  | 0
| 05C5 | [10 empty] | 0
| 05C6 | [10 empty] | 0
| 05C7 | [10 empty] | 0
| 05C8 | [10 empty] | 0
| 05C9 | [10 empty] | 0
| 05CA | [10 empty] | 0
| 05CB | [10 empty] | 0
| 05CC | [10 empty] | 0
| 05CD | [10 empty] | 0
| 05CE | [10 empty] | 0
| 05CF | [10 empty] | 0
| 05D0 | [10 empty] | 0
| 05D1 | [10 empty] | 0
| 05D2 | [10 empty] | 0
| 05D3 | [10 empty] | 0
| 05D4 | [10 empty] | 0
| 05D5 | [10 empty] | 0
| 05D6 | [10 empty] | 0
| 05D7 | [10 empty] | 0
| 05D8 | [10 empty] | 0
| 05D9 | [10 empty] | 0
| 05DA | [10 empty] | 0
| 05DB | [10 empty] | 0
| 05DC | [10 empty] | 0
| 05DD | [10 empty] | 0
| 05DE | [10 empty] | 0
| 05DF | [10 empty] | 0
| 05E0 | [10 empty] | 0
| 05E1 | [10 empty] | 0
| 05E2 | [10 empty] | 0
| 05E3 | [10 empty] | 0
| 05E4 | [10 empty] | 0
| 05E5 | [10 empty] | 0
| 05E6 | [10 empty] | 0
| 05E7 | [10 empty] | 0
| 05E8 | [10 empty] | 0
| 05E9 | [10 empty] | 0
| 05EA | [10 empty] | 0
| 05EB | [10 empty] | 0
| 05EC | [10 empty] | 0
| 05ED | [10 empty] | 0
| 05EE | [10 empty] | 0
| 05EF | [10 empty] | 0
| 05F0 | [10 empty] | 0
| 05F1 | [10 empty] | 0
| 05F2 | [10 empty] | 0
| 05F3 | [10 empty] | 0
battery input(0x0600-0x067F)
| 0600 | AddressMask_Realtime_Input_Bat1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | End user | 00000000 | 0003FFFF
| 0601 | [8 empty] | End user
| 0602 | [8 empty] | End user
| 0603 | [8 empty] | End user
| 0604 | Voltage_Bat1 | U16 | 0.1 | V |  |  | R | No. 1 battery pack voltage | End user | 1 | 16
| 0605 | Current_Bat1 | I16 | 0.01 | A |  |  | R | The charging and discharging current of the first battery pack. Charge is positive, discharge is negative | End user | 1 | 32
| 0606 | Power_Bat1 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the first battery pack. Charge is positive, discharge is negative | End user | 1 | 64
| 0607 | Temperature_Env_Bat1 | I16 | 1 | °C |  |  | R | Ambient temperature of the first battery pack | End user | 1 | 128
| 0608 | SOC_Bat1 | U16 | 1 | % |  |  | R | No. 1 battery pack SOC | End user | 1 | 256
| 0609 | SOH_Bat1 | U16 | 1 | % |  |  | R | No. 1 battery pack SOH | End user | 1 | 512
| 060A | ChargeCycle_Bat1 | U16 | 1 | cycle |  |  | R | Number of cycles of the first battery pack | End user | 1 | 1024
| 060B | Voltage_Bat2 | U16 | 0.1 | V |  |  | R | No. 2 battery pack voltage | End user | 1 | 2048
| 060C | Current_Bat2 | I16 | 0.01 | A |  |  | R | The charging and discharging current of the second battery pack. Charge is positive, discharge is negative | End user | 1 | 4096
| 060D | Power_Bat2 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the second battery pack. Charge is positive, discharge is negative | End user | 1 | 8192
| 060E | Temperature_Env_Bat2 | I16 | 1 | °C |  |  | R | Ambient temperature of the second battery pack | End user | 1 | 16384
| 060F | SOC_Bat2 | U16 | 1 | % |  |  | R | 2nd battery pack SOC | End user | 1 | 32768
| 0610 | SOH_Bat2 | U16 | 1 | % |  |  | R | 2nd battery pack SOH | End user | 1 | 65536
| 0611 | ChargeCycle_Bat2 | U16 | 1 | cycle |  |  | R | Number of cycles of the second battery pack | End user | 1 | 131072
| 0612 | Voltage_Bat3 | U16 | 0.1 | V |  |  | R | No. 3 battery pack voltage | End user |  | 0
| 0613 | Current_Bat3 | I16 | 0.01 | A |  |  | R | The charging and discharging current of the third battery pack. Charge is positive, discharge is negative | End user |  | 0
| 0614 | Power_Bat3 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the third battery pack. Charge is positive, discharge is negative | End user |  | 0
| 0615 | Temperature_Env_Bat3 | I16 | 1 | °C |  |  | R | Ambient temperature of the third battery pack | End user |  | 0
| 0616 | SOC_Bat3 | U16 | 1 | % |  |  | R | No. 3 battery pack SOC | End user |  | 0
| 0617 | SOH_Bat3 | U16 | 1 | % |  |  | R | No. 3 battery pack SOH | End user |  | 0
| 0618 | ChargeCycle_Bat3 | U16 | 1 | cycle |  |  | R | Number of cycles of the third battery pack | End user |  | 0
| 0619 | Voltage_Bat4 | U16 | 0.1 | V |  |  | R | No. 4 battery pack voltage | End user |  | 0
| 061A | Current_Bat4 | I16 | 0.01 | A |  |  | R | Charging and discharging current of No. 4 battery pack. Charge is positive, discharge is negative | End user |  | 0
| 061B | Power_Bat4 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of the 4th battery pack. Charge is positive, discharge is negative | End user |  | 0
| 061C | Temperature_Env_Bat4 | I16 | 1 | °C |  |  | R | Ambient temperature of battery pack No. 4 | End user |  | 0
| 061D | SOC_Bat4 | U16 | 1 | % |  |  | R | No. 4 battery pack SOC | End user |  | 0
| 061E | SOH_Bat4 | U16 | 1 | % |  |  | R | No. 4 battery pack SOH | End user |  | 0
| 061F | ChargeCycle_Bat4 | U16 | 1 | cycle |  |  | R | Number of cycles of the 4th battery pack | End user |  | 0
| 0620 | Voltage_Bat5 | U16 | 0.1 | V |  |  | R | No. 5 battery pack voltage | End user |  | 0
| 0621 | Current_Bat5 | I16 | 0.01 | A |  |  | R | No. 5 battery pack charging and discharging current. Charge is positive, discharge is negative | End user |  | 0
| 0622 | Power_Bat5 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 5 battery pack. Charge is positive, discharge is negative | End user |  | 0
| 0623 | Temperature_Env_Bat5 | I16 | 1 | °C |  |  | R | Ambient temperature of battery pack No. 5 | End user |  | 0
| 0624 | SOC_Bat5 | U16 | 1 | % |  |  | R | No. 5 battery pack SOC | End user |  | 0
| 0625 | SOH_Bat5 | U16 | 1 | % |  |  | R | No. 5 battery pack SOH | End user |  | 0
| 0626 | ChargeCycle_Bat5 | U16 | 1 | cycle |  |  | R | Number of cycles of the 5th battery pack | End user |  | 0
| 0627 | Voltage_Bat6 | U16 | 0.1 | V |  |  | R | No. 6 battery pack voltage | End user |  | 0
| 0628 | Current_Bat6 | I16 | 0.01 | A |  |  | R | No. 6 battery pack charge and discharge current. Charge is positive, discharge is negative | End user |  | 0
| 0629 | Power_Bat6 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 6 battery pack. Charge is positive, discharge is negative | End user |  | 0
| 062A | Temperature_Env_Bat6 | I16 | 1 | °C |  |  | R | Ambient temperature of the 6th battery pack | End user |  | 0
| 062B | SOC_Bat6 | U16 | 1 | % |  |  | R | 6th battery pack SOC | End user |  | 0
| 062C | SOH_Bat6 | U16 | 1 | % |  |  | R | No. 6 battery pack SOH | End user |  | 0
| 062D | ChargeCycle_Bat6 | U16 | 1 | cycle |  |  | R | Number of cycles of the 6th battery pack | End user |  | 0
| 062E | Voltage_Bat7 | U16 | 0.1 | V |  |  | R | No. 7 battery pack voltage | End user |  | 0
| 062F | Current_Bat7 | I16 | 0.01 | A |  |  | R | No. 7 battery pack charging and discharging current. Charge is positive, discharge is negative | End user |  | 0
| 0630 | Power_Bat7 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 7 battery pack. Charge is positive, discharge is negative | End user |  | 0
| 0631 | Temperature_Env_Bat7 | I16 | 1 | °C |  |  | R | Ambient temperature of battery pack No. 7 | End user |  | 0
| 0632 | SOC_Bat7 | U16 | 1 | % |  |  | R | No. 7 battery pack SOC | End user |  | 0
| 0633 | SOH_Bat7 | U16 | 1 | % |  |  | R | No. 7 battery pack SOH | End user |  | 0
| 0634 | ChargeCycle_Bat7 | U16 | 1 | cycle |  |  | R | No. 7 battery pack cycle times | End user |  | 0
| 0635 | Voltage_Bat8 | U16 | 0.1 | V |  |  | R | No. 8 battery pack voltage | End user |  | 0
| 0636 | Current_Bat8 | I16 | 0.01 | A |  |  | R | Charging and discharging current of No. 8 battery pack. Charge is positive, discharge is negative | End user |  | 0
| 0637 | Power_Bat8 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 8 battery pack. Charge is positive, discharge is negative | End user |  | 0
| 0638 | Temperature_Env_Bat8 | I16 | 1 | °C |  |  | R | Ambient temperature of the 8th battery pack | End user |  | 0
| 0639 | SOC_Bat8 | U16 | 1 | % |  |  | R | No. 8 battery pack SOC | End user |  | 0
| 063A | SOH_Bat8 | U16 | 1 | % |  |  | R | No. 8 battery pack SOH | End user |  | 0
| 063B | ChargeCycle_Bat8 | U16 | 1 | cycle |  |  | R | Number of cycles of the 8th battery pack | End user |  | 0
063C
063D
063E
063F
| 0640 | AddressMask_Realtime_Input_Bat2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid. | End user | 00000000 | 0000000F
| 0641 | [8 empty] | End user
| 0642 | [8 empty] | End user
| 0643 | [8 empty] | End user
| 0644 | Voltage_Bat9 | U16 | 0.1 | V |  |  | R | No. 9 battery pack voltage | End user |  | 0
| 0645 | Current_Bat9 | I16 | 0.01 | A |  |  | R | No. 9 battery pack charging and discharging current. Charge is positive, discharge is negative | End user |  | 0
| 0646 | Power_Bat9 | I16 | 0.01 | kW |  |  | R | The charging and discharging power of the 9th battery pack. Charge is positive, discharge is negative | End user |  | 0
| 0647 | Temperature_Env_Bat9 | I16 | 1 | °C |  |  | R | Ambient temperature of the 9th battery pack | End user |  | 0
| 0648 | SOC_Bat9 | U16 | 1 | % |  |  | R | No. 9 battery pack SOC | End user |  | 0
| 0649 | SOH_Bat9 | U16 | 1 | % |  |  | R | No. 9 battery pack SOH | End user |  | 0
| 064A | ChargeCycle_Bat9 | U16 | 1 | cycle |  |  | R | Number of cycles of the 9th battery pack | End user |  | 0
| 064B | Voltage_Bat10 | U16 | 0.1 | V |  |  | R | No. 10 battery pack voltage | End user |  | 0
| 064C | Current_Bat10 | I16 | 0.01 | A |  |  | R | No. 10 battery pack charge and discharge current. Charge is positive, discharge is negative | End user |  | 0
| 064D | Power_Bat10 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 10 battery pack. Charge is positive, discharge is negative | End user |  | 0
| 064E | Temperature_Env_Bat10 | I16 | 1 | °C |  |  | R | Ambient temperature of No. 10 battery pack | End user |  | 0
| 064F | SOC_Bat10 | U16 | 1 | % |  |  | R | No. 10 battery pack SOC | End user |  | 0
| 0650 | SOH_Bat10 | U16 | 1 | % |  |  | R | No. 10 battery pack SOH | End user |  | 0
| 0651 | ChargeCycle_Bat10 | U16 | 1 | cycle |  |  | R | Number of cycles of the 10th battery pack | End user |  | 0
| 0652 | Voltage_Bat11 | U16 | 0.1 | V |  |  | R | No. 11 battery pack voltage | End user |  | 0
| 0653 | Current_Bat11 | I16 | 0.01 | A |  |  | R | The charging and discharging current of No. 11 battery pack. Charge is positive, discharge is negative | End user |  | 0
| 0654 | Power_Bat11 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 11 battery pack. Charge is positive, discharge is negative | End user |  | 0
| 0655 | Temperature_Env_Bat11 | I16 | 1 | °C |  |  | R | Ambient temperature of battery pack No. 11 | End user |  | 0
| 0656 | SOC_Bat11 | U16 | 1 | % |  |  | R | No. 11 battery pack SOC | End user |  | 0
| 0657 | SOH_Bat11 | U16 | 1 | % |  |  | R | No. 11 battery pack SOH | End user |  | 0
| 0658 | ChargeCycle_Bat11 | U16 | 1 | cycle |  |  | R | Number of cycles of the 11th battery pack | End user |  | 0
| 0659 | Voltage_Bat12 | U16 | 0.1 | V |  |  | R | No. 12 battery pack voltage | End user |  | 0
| 065A | Current_Bat12 | I16 | 0.01 | A |  |  | R | Charging and discharging current of No. 12 battery pack. Charge is positive, discharge is negative | End user |  | 0
| 065B | Power_Bat12 | I16 | 0.01 | kW |  |  | R | Charging and discharging power of No. 12 battery pack. Charge is positive, discharge is negative | End user |  | 0
| 065C | Temperature_Env_Bat12 | I16 | 1 | °C |  |  | R | Ambient temperature of the 12th battery pack | End user |  | 0
| 065D | SOC_Bat12 | U16 | 1 | % |  |  | R | No. 12 battery pack SOC | End user |  | 0
| 065E | SOH_Bat12 | U16 | 1 | % |  |  | R | No. 12 battery pack SOH | End user |  | 0
| 065F | ChargeCycle_Bat12 | U16 | 1 | cycle |  |  | R | Number of cycles of the 12th battery pack | End user |  | 0
power(0x0680-0x06BF)
| 0680 | AddressMask_Realtime_ElectricityStatistics1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid. | End user | 00000000 | 0FFFFFFF
| 0681 | [8 empty] | End user
| 0682 | [8 empty] | End user
| 0683 | [8 empty] | End user
| 0684 | PV_Generation_Today | U32 | 0.01 | kWh |  |  | R | Power generation of the day | End user | 1 | 16
| 0685 | [8 empty] | End user | 1 | 32
| 0686 | PV_Generation_Total | U32 | 0.1 | kWh |  |  | R | Total power generation time | End user | 1 | 64
| 0687 | [8 empty] | End user | 1 | 128
| 0688 | Load_Consumption_Today | U32 | 0.01 | kWh |  |  | R | Load power consumption of the day | End user | 1 | 256
| 0689 | [8 empty] | End user | 1 | 512
| 068A | Load_Consumption_Total | U32 | 0.1 | kWh |  |  | R | Total load power consumption | End user | 1 | 1024
| 068B | [8 empty] | End user | 1 | 2048
| 068C | Energy_Purchase_Today | U32 | 0.01 | kWh |  |  | R | Buy electricity on the day | End user | 1 | 4096
| 068D | [8 empty] | End user | 1 | 8192
| 068E | Energy_Purchase_Total | U32 | 0.1 | kWh |  |  | R | Total electricity purchased | End user | 1 | 16384
| 068F | [8 empty] | End user | 1 | 32768
| 0690 | Energy_Selling_Today | U32 | 0.01 | kWh |  |  | R | Electricity sold on the day | End user | 1 | 65536
| 0691 | [8 empty] | End user | 1 | 131072
| 0692 | Energy_Selling_Total | U32 | 0.1 | kWh |  |  | R | Total electricity sold | End user | 1 | 262144
| 0693 | [8 empty] | End user | 1 | 524288
| 0694 | Bat_Charge_Today | U32 | 0.01 | kWh |  |  | R | Battery charge capacity of the day | End user | 1 | 1048576
| 0695 | [8 empty] | End user | 1 | 2097152
| 0696 | Bat_Charge_Total | U32 | 0.1 | kWh |  |  | R | Total battery charge | End user | 1 | 4194304
| 0697 | [8 empty] | End user | 1 | 8388608
| 0698 | Bat_Discharge_Today | U32 | 0.01 | kWh |  |  | R | Battery discharge capacity of the day | End user | 1 | 16777216
| 0699 | [8 empty] | End user | 1 | 33554432
| 069A | Bat_Discharge_Total | U32 | 0.1 | kWh |  |  | R | Total battery discharge | End user | 1 | 67108864
| 069B | [8 empty] | End user | 1 | 134217728
069C
069D
069E
069F
06A0
06A1
06A2
06A3
06A4
06A5
06A6
06A7
06A8
06A9
06AA
06AB
06AC
06AD
06AE
06AF
06B0
06B1
06B2
06B3
06B4
06B5
06B6
06B7
06B8
06B9
06BA
06BB
06BC
06BD
06BE
06BF
internal info(0x06C0-0x06FF)
| 06C0 | AddressMask_Realtime_ClassifiedInfo1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | Installer | 00000000 | 00007FFF
| 06C1 | [8 empty] | Installer
| 06C2 | [8 empty] | Installer
| 06C3 | [8 empty] | Installer
| 06C4 | GFCI | U16 | 1 | mA |  |  | R | Leakage current | Installer | 1 | 16
| 06C5 | Current_Bus_Balance | I16 | 0.01 | A |  |  | R | Balance current | Installer | 1 | 32
| 06C6 | DCI_R | I16 | 1 | mA |  |  | R | R-phase current DC component | Installer | 1 | 64
| 06C7 | DCI_S | I16 | 1 | mA |  |  | R | S-phase current DC component | Installer | 1 | 128
| 06C8 | DCI_T | I16 | 1 | mA |  |  | R | T-phase current DC component | Installer | 1 | 256
| 06C9 | DCV_R | I16 | 1 | mV |  |  | R | R-phase voltage DC component | Installer | 1 | 512
| 06CA | DCV_S | I16 | 1 | mV |  |  | R | S-phase voltage DC component | Installer | 1 | 1024
| 06CB | DCV_T | I16 | 1 | mV |  |  | R | T-phase voltage DC component | Installer | 1 | 2048
| 06CC | Voltage_Bus | U16 | 0.1 | V |  |  | R | Total BUS voltage | Installer | 1 | 4096
| 06CD | Voltage_Bus_P | U16 | 0.1 | V |  |  | R | BUS positive voltage | Installer | 1 | 8192
| 06CE | Voltage_Bus_N | U16 | 0.1 | V |  |  | R | BUS negative voltage | Installer | 1 | 16384
| 06CF | Voltage_Bus_LLC | U16 | 0.1 | V |  |  | R | LLC Bus voltage | Installer |  | 0
| 06D0 | Current_BuckBoost | I16 | 0.01 | A |  |  | R | BuckBoost current | Installer |  | 0
| 06D1 | Voltage_Bus_P_Half | U16 | 0.1 | V |  |  | R | BUS positive half voltage |  |  | 0
| 06D2 | Voltage_Bus_N_Half | U16 | 0.1 | V |  |  | R | BUS negative half voltage |  |  | 0
| 06D3 | FlyingCap_Voltage1 | U16 | 0.1 | V |  |  | R | PV1 flying capacitor voltage |  |  | 0
| 06D4 | FlyingCap_Voltage2 | U16 | 0.1 | V |  |  | R | PV2 flying capacitor voltage |  |  | 0
| 06D5 | FlyingCap_Voltage3 | U16 | 0.1 | V |  |  | R | PV3 flying capacitor voltage |  |  | 0
| 06D6 | FlyingCap_Voltage4 | U16 | 0.1 | V |  |  | R | PV4 flying capacitor voltage |  |  | 0
| 06D7 | FlyingCap_Voltage5 | U16 | 0.1 | V |  |  | R | PV5 flying capacitor voltage |  |  | 0
| 06D8 | FlyingCap_Voltage6 | U16 | 0.1 | V |  |  | R | PV6 flying capacitor voltage |  |  | 0
| 06D9 | FlyingCap_Voltage7 | U16 | 0.1 | V |  |  | R | PV7 flying capacitor voltage |  |  | 0
| 06DA | FlyingCap_Voltage8 | U16 | 0.1 | V |  |  | R | PV8 flying capacitor voltage |  |  | 0
| 06DB | FlyingCap_Voltage9 | U16 | 0.1 | V |  |  | R | PV9 flying capacitor voltage |  |  | 0
| 06DC | FlyingCap_Voltage10 | U16 | 0.1 | V |  |  | R | PV10 flying capacitor voltage |  |  | 0
| 06DD | FlyingCap_Voltage11 | U16 | 0.1 | V |  |  | R | PV11 flying capacitor voltage |  |  | 0
| 06DE | FlyingCap_Voltage12 | U16 | 0.1 | V |  |  | R | PV12 flying capacitor voltage |  |  | 0
| 06DF | FlyingCap_Voltage13 | U16 | 0.1 | V |  |  | R | PV13 flying capacitor voltage |  |  | 0
| 06E0 | FlyingCap_Voltage14 | U16 | 0.1 | V |  |  | R | PV14 flying capacitor voltage |  |  | 0
| 06E1 | FlyingCap_Voltage15 | U16 | 0.1 | V |  |  | R | PV15 flying capacitor voltage |  |  | 0
| 06E2 | FlyingCap_Voltage16 | U16 | 0.1 | V |  |  | R | PV16 flying capacitor voltage |  |  | 0
06E3
06E4
06E5
06E6
06E7
06E8
06E9
06EA
06EB
06EC
06ED
06EE
06EF
06F0
06F1
06F2
06F3
06F4
06F5
06F6
06F7
06F8
06F9
06FA
06FB
06FC
06FD
06FE
06FF
combined info(0x0700-0x077F)
| 0700 | AddressMask_Realtime_CombinerInfo1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | Installer | 00000000 | 0000000F
| 0701 | [8 empty] | Installer
| 0702 | [8 empty] | Installer
| 0703 | [8 empty] | Installer
| 0704 | Voltage_Group1 | U16 | 0.1 | V |  |  | R | The first group of bus voltage |  | 0 | 0
| 0705 | Current_Group1_Branch1 | U16 | 0.01 | A |  |  | R | The first group of the first string current
| 0706 | Current_Group1_Branch2 | U16 | 0.01 | A |  |  | R | The first group and the second string current
| 0707 | Voltage_Group2 | U16 | 0.1 | V |  |  | R | The second group of bus voltage
| 0708 | Current_Group2_Branch1 | U16 | 0.01 | A |  |  | R | 2nd group 1st string current
| 0709 | Current_Group2_Branch2 | U16 | 0.01 | A |  |  | R | 2nd group 2nd string current
| 070A | Voltage_Group3 | U16 | 0.1 | V |  |  | R | The third group of bus voltage
| 070B | Current_Group3_Branch1 | U16 | 0.01 | A |  |  | R | 3rd group 1st string current
| 070C | Current_Group3_Branch2 | U16 | 0.01 | A |  |  | R | 3rd group 2nd string current
| 070D | Voltage_Group4 | U16 | 0.1 | V |  |  | R | Group 4 bus voltage
| 070E | Current_Group4_Branch1 | U16 | 0.01 | A |  |  | R | 4th group 1st string current
| 070F | Current_Group4_Branch2 | U16 | 0.01 | A |  |  | R | 4th group 2nd string current
| 0710 | Voltage_Group5 | U16 | 0.1 | V |  |  | R | Group 5 bus voltage
| 0711 | Current_Group5_Branch1 | U16 | 0.01 | A |  |  | R | 5th group 1st string current
| 0712 | Current_Group5_Branch2 | U16 | 0.01 | A |  |  | R | 5th group 2nd string current
| 0713 | Voltage_Group6 | U16 | 0.1 | V |  |  | R | Group 6 bus voltage
| 0714 | Current_Group6_Branch1 | U16 | 0.01 | A |  |  | R | 6th group 1st string current
| 0715 | Current_Group6_Branch2 | U16 | 0.01 | A |  |  | R | 6th group 2nd string current
| 0716 | Voltage_Group7 | U16 | 0.1 | V |  |  | R | Group 7 bus voltage
| 0717 | Current_Group7_Branch1 | U16 | 0.01 | A |  |  | R | 7th group 1st string current
| 0718 | Current_Group7_Branch2 | U16 | 0.01 | A |  |  | R | 7th group 2nd string current
| 0719 | Voltage_Group8 | U16 | 0.1 | V |  |  | R | Group 8 bus voltage
| 071A | Current_Group8_Branch1 | U16 | 0.01 | A |  |  | R | 8th group 1st string current
| 071B | Current_Group8_Branch2 | U16 | 0.01 | A |  |  | R | 8th group 2nd string current
| 071C | Voltage_Group9 | U16 | 0.1 | V |  |  | R | Group 9 bus voltage
| 071D | Current_Group9_Branch1 | U16 | 0.01 | A |  |  | R | 9th group 1st string current
| 071E | Current_Group9_Branch2 | U16 | 0.01 | A |  |  | R | 9th group 2nd string current
| 071F | Voltage_Group10 | U16 | 0.1 | V |  |  | R | Group 10 bus voltage
| 0720 | Current_Group10_Branch1 | U16 | 0.01 | A |  |  | R | 10th group 1st string current
| 0721 | Current_Group10_Branch2 | U16 | 0.01 | A |  |  | R | 10th group 2nd string current
| 0722 | Voltage_Group11 | U16 | 0.1 | V |  |  | R | Group 11 bus voltage
| 0723 | Current_Group11_Branch1 | U16 | 0.01 | A |  |  | R | 11th group 1st string current
| 0724 | Current_Group11_Branch2 | U16 | 0.01 | A |  |  | R | 11th group 2nd string current
| 0725 | Voltage_Group12 | U16 | 0.1 | V |  |  | R | The 12th group of bus voltage
| 0726 | Current_Group12_Branch1 | U16 | 0.01 | A |  |  | R | 12th group 1st string current
| 0727 | Current_Group12_Branch2 | U16 | 0.01 | A |  |  | R | 12th group 2nd string current
| 0728 | Voltage_Group13 | U16 | 0.1 | V |  |  | R | Group 13 bus voltage
| 0729 | Current_Group13_Branch1 | U16 | 0.01 | A |  |  | R | 13th group 1st string current
| 072A | Current_Group13_Branch2 | U16 | 0.01 | A |  |  | R | 13th group 2nd string current
| 072B | Voltage_Group14 | U16 | 0.1 | V |  |  | R | Group 14 bus voltage
| 072C | Current_Group14_Branch1 | U16 | 0.01 | A |  |  | R | The 14th group and the 1st string current
| 072D | Current_Group14_Branch2 | U16 | 0.01 | A |  |  | R | The 14th group and the 2nd string current
| 072E | Voltage_Group15 | U16 | 0.1 | V |  |  | R | Group 15 bus voltage
| 072F | Current_Group15_Branch1 | U16 | 0.01 | A |  |  | R | 15th group 1st string current
| 0730 | Current_Group15_Branch2 | U16 | 0.01 | A |  |  | R | 15th group 2nd string current
| 0731 | Voltage_Group16 | U16 | 0.1 | V |  |  | R | The 16th group of bus voltage
| 0732 | Current_Group16_Branch1 | U16 | 0.01 | A |  |  | R | The 16th group of the first string current
| 0733 | Current_Group16_Branch2 | U16 | 0.01 | A |  |  | R | 16th group 2nd string current
0734
0735
0736
0737
0738
0739
073A
073B
073C
073D
073E
073F
| 0740 | AddressMask_Realtime_CombinerInfo2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | Installer | 00000000 | 0000000F
| 0741 | [8 empty] | Installer
| 0742 | [8 empty] | Installer
| 0743 | [8 empty] | Installer
| 0744 | [9 empty] | 0 | 0
0745
0746
0747
0748
0749
074A
074B
074C
074D
074E
074F
0750
0751
0752
0753
0754
0755
0756
0757
0758
0759
075A
075B
075C
075D
075E
075F
0760
0761
0762
0763
0764
0765
0766
0767
0768
0769
076A
076B
076C
076D
076E
076F
0770
0771
0772
0773
0774
0775
0776
0777
0778
0779
077A
077B
077C
077D
077E
077F
Arcing information(0x0780-0x07BF)
| 0780 | AddressMask_Realtime_ArcInfo3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | Installer | 00000000 | 0000000F
| 0781 | [8 empty] | Installer
| 0782 | [8 empty] | Installer
| 0783 | [8 empty] | Installer
| 0784 | ArcStrength_Channel1 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 1 |  |  | 0
| 0785 | ArcStrength_Channel2 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 2 |  |  | 0
| 0786 | ArcStrength_Channel3 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 3 |  |  | 0
| 0787 | ArcStrength_Channel4 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 4 |  |  | 0
| 0788 | ArcStrength_Channel5 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 5 |  |  | 0
| 0789 | ArcStrength_Channel6 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 6 |  |  | 0
| 078A | ArcStrength_Channel7 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 7 |  |  | 0
| 078B | ArcStrength_Channel8 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 8 |  |  | 0
| 078C | ArcStrength_Channel9 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 9 |  |  | 0
| 078D | ArcStrength_Channel10 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 10 |  |  | 0
| 078E | ArcStrength_Channel11 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 11 |  |  | 0
| 078F | ArcStrength_Channel12 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 12 |  |  | 0
| 0790 | ArcStrength_Channel13 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 13 |  |  | 0
| 0791 | ArcStrength_Channel14 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 14 |  |  | 0
| 0792 | ArcStrength_Channel15 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 15 |  |  | 0
| 0793 | ArcStrength_Channel16 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 16 |  |  | 0
| 0794 | ArcStrength_Channel17 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 17 |  |  | 0
| 0795 | ArcStrength_Channel18 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 18 |  |  | 0
| 0796 | ArcStrength_Channel19 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 19 |  |  | 0
| 0797 | ArcStrength_Channel20 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 20 |  |  | 0
| 0798 | ArcStrength_Channel21 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 21 |  |  | 0
| 0799 | ArcStrength_Channel22 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 22 |  |  | 0
| 079A | ArcStrength_Channel23 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 23 |  |  | 0
| 079B | ArcStrength_Channel24 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 24 |  |  | 0
| 079C | ArcStrength_Channel25 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 25 |  |  | 0
| 079D | ArcStrength_Channel26 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 26 |  |  | 0
| 079E | ArcStrength_Channel27 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 27 |  |  | 0
| 079F | ArcStrength_Channel28 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 28 |  |  | 0
| 07A0 | ArcStrength_Channel29 | I16 | 1 |  |  |  | R | Channel 29 monitored real-time arc intensity |  |  | 0
| 07A1 | ArcStrength_Channel30 | I16 | 1 |  |  |  | R | Real-time arc intensity monitored by channel 30 |  |  | 0
| 07A2 | ArcStrength_history_Channel1 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 1 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07A3 | ArcStrength_history_Channel2 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 2 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07A4 | ArcStrength_history_Channel3 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 3 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07A5 | ArcStrength_history_Channel4 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 4 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07A6 | ArcStrength_history_Channel5 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 5 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07A7 | ArcStrength_history_Channel6 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 6 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07A8 | ArcStrength_history_Channel7 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 7 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07A9 | ArcStrength_history_Channel8 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 8 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07AA | ArcStrength_history_Channel9 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 9 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07AB | ArcStrength_history_Channel10 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 10 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07AC | ArcStrength_history_Channel11 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 11 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07AD | ArcStrength_history_Channel12 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 12 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07AE | ArcStrength_history_Channel13 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 13 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07AF | ArcStrength_history_Channel14 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 14 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07B0 | ArcStrength_history_Channel15 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 15 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07B1 | ArcStrength_history_Channel16 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 16 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07B2 | ArcStrength_history_Channel17 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 17 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07B3 | ArcStrength_history_Channel18 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 18 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07B4 | ArcStrength_history_Channel19 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 19 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07B5 | ArcStrength_history_Channel20 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 20 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07B6 | ArcStrength_history_Channel21 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 21 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07B7 | ArcStrength_history_Channel22 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 22 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07B8 | ArcStrength_history_Channel23 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 23 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07B9 | ArcStrength_history_Channel24 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 24 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07BA | ArcStrength_history_Channel25 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 25 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07BB | ArcStrength_history_Channel26 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 26 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07BC | ArcStrength_history_Channel27 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 27 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07BD | ArcStrength_history_Channel28 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 28 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07BE | ArcStrength_history_Channel29 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 29 is powered on Maximum value, automatically cleared after power failure |  |  | 0
| 07BF | ArcStrength_history_Channel30 | I16 | 1 |  |  |  | R | Record the monitored arc intensity history after channel 30 is powered on Maximum value, automatically cleared after power failure |  |  | 0
Basic setting(0x1000-0x17FF)
Basic parameter configuration(0x1000-0x10FF)
| 1000 | AddressMask_Config_Basic1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | End user | 01FF63FE | 001EFFFF
| 1001 | [8 empty] | End user
| 1002 | [8 empty] | End user
| 1003 | [8 empty] | End user
| 1004 | SysTimeConfig_Year | U16 |  | Year | 0 | 99 | RW | System time-year; The actual year is equal to 2000+register value | End user | 1 | 16
| 1005 | SysTimeConfig_Month | U16 |  | January | 1 | 12 | RW | System time-month | End user | 1 | 32
| 1006 | SysTimeConfig_Date | U16 |  | Day | 1 | 31 | RW | System Time-Daily Minutes | End user | 1 | 64
| 1007 | SysTimeConfig_Hour | U16 |  | hour | 0 | 23 | RW | System time-hour | End user | 1 | 128
| 1008 | SysTimeConfig_Minute | U16 |  | minutes | 0 | 59 | RW | System time-minutes | End user | 1 | 256
| 1009 | SysTimeConfig_Second | U16 |  | seconds | 0 | 59 | RW | System time-second | End user | 1 | 512
| 100A | SysTimeConfig_Control | U16 |  |  | 1 | 1 | RW | When the written value is 1, the value in the system time shadow register is updated to the actual system time; When reading, return the status of the last write operation: 0x0000: success 0x0001: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter access failed 0xFFFF: The operation failed, the input parameter is wrong | End user | 1 | 1024
| 100B | RS485Config_Address | U16 |  |  | 1 | 247 | RW | RS485 configuration-address | End user | 1 | 2048
| 100C | RS485Config_Baud | U16 |  |  | 0 | 4 | RW | RS485波特率选择； 0：4800bps 1：9600bps（默认） 2：19200bps 3：38400bps 4：57600bps | End user | 1 | 4096
| 100D | RS485Config_StopBit | U16 |  |  | 0 | 2 | RW | RS485 stop bit selection; 0: 1 stop bit (default) 1: 1.5 stop bits 2: 2 stop bits | End user | 1 | 8192
| 100E | RS485Config_ParityBit | U16 |  |  | 0 | 4 | RW | RS485 check digit selection; 0: No check/None (default) 1: Even parity/Even 2: Odd parity/Odd 3: High/Mark 4: Low/Space | End user | 1 | 16384
| 100F | RS485Config_Control | U16 |  |  | 1 | 1 | RW | When the written value is 1, the value in the RS485 configuration shadow register is updated to the system RS485 configuration; When reading, return the status of the last write operation: 0x0000: success 0x0001: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter access failed 0xFFFF: The operation failed, the input parameter is wrong | End user | 1 | 32768
| 1010 | PV_InputMode_Config | U16 |  |  | 0 | 1 | RW | PV input mode selection. 0: Parallel mode 1: Independent mode (default) | Installer |  | 0
| 1011 | InputType_Channel0_Config | U16 |  |  | 0 | 255 | RW | Input channel 0 type selection. The value 0 indicates that the current channel is not in use. Values 1 to 127 indicate that the current channel is a photovoltaic panel input. values 128 to 255 indicate that the current channel is a battery input. If two or more channels have the same value and are greater than zero, it means that these channels are input in parallel; | Installer | 1 | 131072
| 1012 | InputType_Channel1_Config | U16 |  |  | 0 | 255 | RW |  | Installer | 1 | 262144
| 1013 | InputType_Channel2_Config | U16 |  |  | 0 | 255 | RW |  | Installer | 1 | 524288
| 1014 | InputType_Channel3_Config | U16 |  |  | 0 | 255 | RW |  | Installer | 1 | 1048576
| 1015 | InputType_Channel4_Config | U16 |  |  | 0 | 255 | RW |  | Installer |  | 0
| 1016 | InputType_Channel5_Config | U16 |  |  | 0 | 255 | RW |  | Installer |  | 0
| 1017 | InputType_Channel6_Config | U16 |  |  | 0 | 255 | RW |  | Installer |  | 0
| 1018 | InputType_Channel7_Config | U16 |  |  | 0 | 255 | RW |  | Installer |  | 0
| 1019 | InputType_Channel8_Config | U16 |  |  | 0 | 255 | RW |  | Installer |  | 0
| 101A | InputType_Channel9_Config | U16 |  |  | 0 | 255 | RW |  | Installer |  | 0
| 101B | InputType_Channel10_Config | U16 |  |  | 0 | 255 | RW |  | Installer |  | 0
| 101C | InputType_Channel11_Config | U16 |  |  | 0 | 255 | RW |  | Installer |  | 0
| 101D | InputType_Channel12_Config | U16 |  |  | 0 | 255 | RW |  | Installer |  | 0
| 101E | InputType_Channel13_Config | U16 |  |  | 0 | 255 | RW |  | Installer |  | 0
| 101F | InputType_Channel14_Config | U16 |  |  | 0 | 255 | RW |  | Installer |  | 0
| 1020 | InputType_Channel15_Config | U16 |  |  | 0 | 255 | RW |  | Installer |  | 0
| 1021 | InputType_Control | U16 |  |  | 1 | 1 | RW | When the written value is 1, the value in the input channel type shadow register is updated to the system input channel type configuration; When reading, return the status of the last write operation: 0x0000: success 0x0001: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter access failed 0xFFFF: The operation failed, the input parameter is wrong | Installer | 1 | 8589934592
| 1022 | SafetyUpdateFromUSB_Control | U16 |  |  | 1 | 1 | RW | When the written value is 1, it is used for the communication board to take out the safety parameters from the U disk; When reading, return the status of the last write operation: 0x0000: success 0x0001: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter access failed 0xFFFF: The operation failed, the input parameter is wrong | Installer | 1 | 17179869184
| 1023 | AntiReflux_Control | U16 |  |  | 0 | 2 | RW | Anti-backflow enable control When the written value is 0, the anti-backflow function is prohibited When the written value is 1, it is the default anti-backflow mode When the written value is 2, it is the average power anti-backflow mode | Installer | 1 | 34359738368
| 1024 | AntiReflux_Power | U16 | 100 | W | 0 | 65535 | RW | Anti-backflow power | Installer | 1 | 68719476736
| 1025 | IVCurveScan_Control | U16 |  |  | 0 | 1 | RW | IV curve scan enable control | Installer | 1 | 137438953472
| 1026 | IVCurveScan_Period | U16 | 1 | Minutes | 5 | 65535 | RW | IV curve scan period | Installer | 1 | 274877906944
| 1027 | IVCurveScan_Oneshot | U16 |  |  | 1 | 1 | RW | IV curve scan activated; When the written value is 1, activate 1 IV curve scan; When reading, return the status of the last write operation: 0x0000: success 0x0001: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter access failed 0xFFFF: The operation failed, the input parameter is wrong | Installer | 1 | 549755813888
| 1028 | IVCurveScan_ReadChannel | U16 |  |  | 0 | 31 | RW | The IV curve scan returns the data channel. This register is used to specify the PV channel corresponding to the return value of the IV curve scan result | Installer | 1 | 1099511627776
| 1029 | EPS_Control | U16 |  |  | 0 | 2 | RW | Emergency power supply enable control 0: Turn off the emergency power supply (default) 1: Turn on the emergency power supply and prohibit cold start 2: Turn on the emergency power supply and enable cold start | End user | 1 | 2199023255552
| 102A | EPS_WaitTime | U16 | 1 | seconds | 0 | 65535 | RW | Emergency power supply start waiting time (reserved function) | End user |  | 0
| 102B | BatteryActive_Control | U16 |  |  | 0 | 1 | RW | Battery automatic activation enable control | End user |  | 0
| 102C | BatteryActive_Oneshot | U16 |  |  | 1 | 1 | RW | Battery activation; When the written value is 1, the battery is activated once; When reading, return the status of the last write operation: 0x0000: success 0x0001: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter storage failed 0xFFFF: The operation failed, the input parameter is wrong | End user | 0 | 0
| 102D | CT_Auto_Calibrate | U16 |  |  | 1 | 1 | RW | CT automatic correction; When the written value is 1, automatic CT correction is performed once; When reading, return the status of the last write operation: 0x0000: success 0x0001: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter storage failed 0xFFFF: The operation failed, the input parameter is wrong | Installer | 1 | 35184372088832
| 102E | Italy_AutoTest | U16 |  |  | 1 | 2 | RW | 意大利自动测试 写入： 0x0001：执行标准测试； 0x0002：执行快速测试； 读取时，返回上次写入操作的状态： 0x0000：成功 0x0001：正在操作标准测试 0x0002：正在操作快速测试 0xFFFB：操作失败，控制器拒绝响应（可能控制器正忙或配置错误） 0xFFFC：操作失败，控制器无应答 0xFFFD：操作失败，当前功能被禁止 0xFFFE：操作失败，参数存储失败 0xFFFF：操作失败，输入参数有误 | Installer | 1 | 70368744177664
| 102F |  | U16 |  |  |  |  | RW |  | Installer |  | 0
| 1030 | EnergyStatistics_Date_Year | U16 | 1 | Year | 0 | 19 | RW | Energy statistics return date setting register. This register specifies the year of the returned energy data. Year refers to the Nth most recent year relative to the inverter system time. N is the register value. 0: the current year of the system time; 1: 1 year before the system time; … 19: 19 years before system time | Installer | 1 | 281474976710656
| 1031 | EnergyStatistics_Date_Month | U16 | 1 | Month | 1 | 12 | RW | Energy statistics return date setting register. This register specifies the month of the returned energy data. | Installer | 1 | 562949953421312
| 1032 | EnergyStatistics_Date_Date | U16 | 1 | Date | 1 | 31 | RW | Energy statistics return date setting register. This register specifies the day and minute of the returned energy data | Installer | 1 | 1125900000000000
| 1033 | EnergyStatistics_Config | U16 |  |  |  |  | RW | Energy statistics return setting register. High byte: the date and time setting of the returned data. 0x01: Every day, the first 24 data in the return area are valid; 0x02: every month, the first 31 data in the return area are valid; 0x03: Every year, the first 12 data in the return area are valid; 0x04: life cycle, the first 20 data in the return area are valid; Other: invalid. Low byte: the physical quantity setting of the returned data. 0x01: photovoltaic power generation; 0x02: load power consumption; 0x03: The system buys electricity; 0x04: The system sells electricity; 0x05: battery charge capacity; 0x06: battery discharge capacity; Other: invalid. | Installer | 1 | 2251800000000000
| 1034 | Language | U16 |  |  | 0 | 65535 | RW | The inverter menu language number setting register. 0: 1: | End user | 1 | 4503600000000000
| 1035 | Parallel_Control | U16 |  |  | 0 | 2 | RW | 0: Disable the parallel function 1: Enable AC parallel function 2: Enable AC+BAT parallel function | Installer | 1 | 9007200000000000
| 1036 | Parallel_Master_Slave | U16 |  |  | 0 | 1 | RW | 0: The machine is configured as a slave 1: The machine is configured as the host (default) | Installer | 1 | 18014400000000000
| 1037 | Parallel_Address | U16 |  |  | 0 | 10 | RW | Local parallel address | Installer | 1 | 36028800000000000
| 1038 | UnbalancedSupport_Control | U16 |  |  | 0 | 1 | RW | 3-phase 4-wire mode grid unbalanced support control register 0: Disable unbalanced support function (default) 1: Enable unbalanced support function | Installer | 1 | 72057600000000000
| 1039 | PV_Generation_Ratio | U16 | 0.001 | p.u. | 800 | 3600 | RW | Power generation rate. The default value is 1000 | Installer |  | 0
| 103A | Energy_Purchase_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | Buy power rate. The default value is 1000 | Installer |  | 0
| 103B | Energy_Selling_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | Selling power ratio. The default value is 1000 | Installer |  | 0
| 103C | Bat_Charge_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | Battery Charging power rate, Default value: 1000 | Installer |  | 0
| 103D | Bat_Discharge_Ratio | U16 | 0.001 | p.u. | 800 | 1500 | RW | Battery Discharge power rate. Default value: 1000 | Installer |  | 0
103E
103F
| 1040 | AddressMask_Config_Basic2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid. | End user | 00000000 | 000FFFFF
| 1041 | [8 empty] | End user
| 1042 | [8 empty] | End user
| 1043 | [8 empty] | End user
| 1044 | BatConfig_ID | U16 |  |  | 0 | 7 | RW | Battery serial number. The serial number specified by this register corresponds to the actual battery input interface of the inverter. After successfully writing to this register, the battery parameters will be updated to the parameters corresponding to the written serial number. NOTE: the BatConfig parameters can only be written all at once with Multi write command, for example: 01 10 10 44 00 13 26 00 00 00 00 00 00 13 88 16 F3 00 00 11 17 0D AC 0D AC 00 32 00 32 00 78 13 88 00 00 00 05 00 01 00 10 00 10 00 10 B7 B8 | End user | 1 | 16
| 1045 | BatConfig_Address | U16 |  |  | 0 | 99 | RW | Battery communication address. If multiple batteries are allowed in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number | End user | 1 | 32
| 1046 | BatConfig_Protocol | U16 |  |  | 0 | 65535 | RW | Battery Parameters-Communication Protocol 0: Built-in BMS (for batteries without their own BMS like Lead Acid) 1: Pylontech Protocol 2: SOFAR Protocol 3: AMASS Batteries 4: LGchem 5: Alpha.ESS 6: CATL 7: Weco | End user | 1 | 64
| 1047 | BatConfig_Voltage_Over | U16 | 0.1 | V | 0 | 65535 | RW | Battery parameters-overvoltage protection value | Installer | 1 | 128
| 1048 | BatConfig_Voltage_Charge | U16 | 0.1 | V | 0 | 65535 | RW | Battery parameters-charging voltage protection value | Installer | 1 | 256
| 1049 | BatConfig_Voltage_Lack | U16 | 0.1 | V | 0 | 65535 | RW | Battery parameters-undervoltage protection voltage, lead-acid battery visible | Installer | 1 | 512
| 104A | BatConfig_Voltage_Discharge_Stop | U16 | 0.1 | V | 0 | 65535 | RW | Battery Parameter-Lowest discharge voltage | Installer | 1 | 1024
| 104B | BatConfig_Current_Charge_Limit | U16 | 0.01 | A | 0 | 65535 | RW | Battery Parameter-Maximum charge current limit | End user | 1 | 2048
| 104C | BatConfig_Current_Discharge_Limit | U16 | 0.01 | A | 0 | 65535 | RW | Battery Parameter-Maximum discharge current limit | End user | 1 | 4096
| 104D | BatConfig_Depth_of_Discharge | U16 | 1 | % | 1 | 90 | RW | Dod indicates the max discharge power, when SOC<1-DOD, inverter will stop power discharge , inverter will stop power discharge caused by other issues. DOD<=EOD | End user | 1 | 8192
| 104E | BatConfig_End_of_Discharge | U16 | 1 | % | 1 | 90 | RW | EOD indicates the maximum off-grid discharge. When SOC<1-EOD, the inverter will stop discharging, and the inverter will also stop discharging according to other conditions | End user | 1 | 16384
| 104F | BatConfig_Capacity | U16 | 1 | Ah | 1 | 65535 | RW | Battery parameters-battery capacity (default 50) | End user | 1 | 32768
| 1050 | BatConfig_Voltage_Nominal | U16 | 0.1 | V | 0 | 65535 | RW | Battery parameters-rated battery voltage (default 0) | End user | 1 | 65536
| 1051 | BatConfig_Cell_Type | U16 | 1 |  | 0 | 3 | RW | Battery parameters-battery cell type; 0: Lead acid (default) 1: Lithium iron phosphate 2: Lithium Ternary battery 3: Lithium titanate battery | End user | 1 | 131072
| 1052 | BatConfig_EPS_Buffer | U16 | 1 | % | 5 | 100 | RW | Battery parameters-lead acid resistance; Default value: 50mΩ; Internal resistance + line resistance | End user | 1 | 262144
| 1053 | BatConfig_Control | U16 |  |  |  |  | RW | Battery parameter write control; When the written value is 1, the value in the battery parameter shadow register is updated to the system battery parameter configuration; When the written value is 2, the value in the battery parameter shadow register is updated to the default value of BatConfig_Potocol; When reading, return the status of the last write operation: 0x0000: success 0x0001: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter storage failed 0xFFFF: The operation failed, the input parameter is wrong | End user | 1 | 524288
| 1054 | BatConfig_Address2 | U16 |  |  | 0 | 99 | RW | Battery address. If multiple batteries are allowed in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number | End user | 1
| 1055 | BatConfig_Address3 | U16 |  |  | 0 | 99 | RW | Battery address. If multiple batteries are allowed in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number. | End user | 1
| 1056 | BatConfig_Address4 | U16 |  |  | 0 | 99 | RW | Battery address. If multiple batteries are allowed in the system, this register is used to mark the battery address of the physical interface corresponding to the battery serial number. | End user | 1
1057
1058
1059
105A
105B
105C
105D
105E
105F
| 1060 | PCCSampleMode | U16 |  |  | 0 | 2 | RW | PCC power acquisition device configuration 0: not used 1: Electricity meter 2: CT 3: ARPC
1061
1062
1063
1064
1065
1066
1067
1068
1069
106A
106B
106C
106D
106E
106F
1070
1071
1072
1073
1074
1075
1076
1077
1078
1079
107A
107B
107C
107D
107E
107F
| 1080 | AddressMask_Config_Basic3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid | Installer | 00000000 | 0000000F
| 1081 | [8 empty] | Installer
| 1082 | [8 empty] | Installer
| 1083 | [8 empty] | Installer
| 1084 | Arcing_Alarm_Enable | U16 |  |  |  |  | RW | Enable arc detection function | Installer
| 1085 | Arcing_ChannelSelfTest_Comm | U16 |  |  |  |  | RW | Write 1 to start self-check (self-check all channels). It will be automatically cleared after the self-test | Installer
| 1086 | Arcing_ChannelSelfTest_Result | U32 |  |  |  |  | R | bit0 indicates the self-check result of channel 1, bit1 indicates the channel The self-check result of 2, bit2 represents the self-check result of channel 3 If the result, bit3 represents the self-check result of channel 4. 1 means self-test failed (or no self-test), 0 means self-test The inspection is successful | Installer
| 1087 | [8 empty] | Installer
| 1088 | Arcing_Alarm_Threshold1 | I16 | 1 |  | 0 | 127 | RW | Settable arc alarm threshold (all channels) | Installer
| 1089 | Arcing_Alarm_Threshold2 | I16 | 1 |  | 0 | 127 | RW | Settable arc alarm threshold (all channels) | Installer
| 108A | Arcing_Alarm_Threshold3 | I16 | 1 |  | 0 | 127 | RW | Settable arc alarm threshold (all channels) | Installer
| 108B | Arcing_Alarm_Threshold4 | I16 | 1 |  | 0 | 127 | RW | Settable arc alarm threshold (all channels) | Installer
| 108C | Arcing_Alarm_Clear | U16 |  |  | 0x1234 | 0x1234 | RW | Write 0x1234 to clear the arc alarm (all channels) | Installer
| 108D | Arcing_Alarm_ShutDown_Threshold | U16 | 1 |  | 1 | 32 | RW | DC arc alarm fault threshold: after "current arc alarm times" is greater than or equal to "current arc alarm times", a DC arc alarm fault is reported and the inverter shuts down | Installer
| 108E | Arcing_Alarm_Counter | U16 | 1 |  | 0 | 32 | R | Current arc alarm times | Installer
108F
1090
1091
1092
1093
1094
1095
1096
1097
1098
1099
109A
109B
109C
109D
109E
109F
| 10A0 | PLC_Enable_Setting | U16 |  |  |  |  | RW
| 10A1 | PLC_Com_Property | U16 | NULL | NULL |  |  | RW | bit0-bit1:0~1 corresponds to 1/1.5 bit2~bit4:0~7 corresponds to NONE/odd/EVEN three kinds of checksum bit5~bit7 0~3 corresponds to 8/9l two kinds of data bit length bit8~15 0~7 corresponds to 4800/9600/19200/38400/115200 | End-users
10A2
10A3
10A4
| 10A5 | BLE_Enable_Setting | U16 | NULL | NULL |  | 1 | RW
| 10A6 | BLE_Com_Property | U16 | NULL | NULL |  | 65535 | RW | bit0-bot1:0~1 corresponds to 1/1.5 bit2~bit4:0~7 corresponds to NONE/odd/EVEN three types of checksum bit5~bit7 0~1 corresponds to 8/9l two kinds of data bit length bit8~15 0~7 corresponds to 4800/9600/19200/38400/115200
10A7
10A8
10A9
10AA
10AB
10AC
10AD
10AE
10AF
| 10B0 | PID_Auto_running_enable | U16 |  |  |  | 1 | RW | PID start auto-run. 0 means disable; 1 means enable. | End Users
| 10B1 | PID_Working_Start_Time | BCD16 | 1 | Minute |  | 2359 | RW | PID operation start time (BCD code). For example: a minimum value of 0x0000 indicates 00:00. Maximum value 0x2359 indicates 23:59. | End User
| 10B2 | PID_Working_Hours | U16 | 1 | Minute |  | 65535 | RW | PID operating duration. | End User
| 10B3 | PID_Working_PV_Threshold | U16 | 0.1 | V |  | 65535 | RW | PID start PV value threshold. PID activation is only allowed when the PV voltage is below the threshold value. | End User
| 10B4 | PID_Break_Restart_Delay | U16 | 1 | Minute |  | 65535 | RW | Restart wait time after PID fault shutdown. | End User
10B5
10B6
10B7
10B8
10B9
10BA
10BB
10BC
10BD
10BE
10BF
10C0
10C1
10C2
10C3
10C4
10C5
10C6
10C7
10C8
10C9
10CA
10CB
10CC
10CD
10CE
10CF
10D0
10D1
10D2
10D3
10D4
10D5
10D6
10D7
10D8
10D9
10DA
10DB
10DC
10DD
10DE
10DF
10E0
10E1
10E2
10E3
10E4
10E5
10E6
10E7
10E8
10E9
10EA
10EB
10EC
10ED
10EE
10EF
10F0
10F1
10F2
10F3
10F4
10F5
10F6
10F7
10F8
10F9
10FA
10FB
10FC
10FD
10FE
10FF
Remote control (0x1100-0x12FF)
| 1100 | AddressMask_Config_Remote1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above and including the address of this field. bit4 represents the address where the highest bit of this field plus 1 is located. 0 means invalid; 1 means valid. | End user | 000083FF | 87FF001F
| 1101 | [8 empty] | End user
| 1102 | [8 empty] | End user
| 1103 | [8 empty] | End user
| 1104 | Remote_On_Off_Control | U16 |  |  | 0 | 1 | RW | Remote power on/off. 0x0000: Power off 0x0001: power on | End user | 1 | 16
| 1105 | Power_Control | U16 |  |  |  |  | RW | Power control. Bit0: active (address 0x1106) enable bit Bit1: Reactive (address 0x1107-0x1108) enable bit Bit2: Reactive mode selection bit (0: Reactive_Power; 1: Power_Factor) | End user |  | 0
| 1106 | Active_Power_Export_Limit | U16 | 0.1 | % | 0 | 1000 | RW | Output maximum active power percentage | End user |  | 0
| 1107 | Active_Power_Import_Limit | U16 | 0.1 | % | 0 | 1000 | RW | Input maximum active power percentage | End user |  | 0
| 1108 | Reactive_Power_Setting | I16 | 0.1 | % | -1000 | 1000 | RW | Reactive power percentage. The inverter end is positive for leading and negative for lagging Note: Maximum reactive power is limited by the specific model. | End user |  | 0
| 1109 | Power_Factor_Setting | I16 | 0.01 | p.u. | -100 | 100 | RW | Power factor. The inverter end is positive for leading and negative for lagging Note: Minimum power factor is limited by the specific model. | End user |  | 0
| 110A | Active_Power_Limit_Speed | U16 | 1 | % | 1 | 65535 | RW | Active power limit change rate | End user |  | 0
| 110B | Reactive_Power_Response_Time | U16 | 0.1 | second | 0 | 65535 | RW | Reactive power setting response time | End user |  | 0
| 110C | [8 empty] | End user |  | 0
| 110D | [8 empty] | End user |  | 0
| 110E | [8 empty] | End user |  | 0
| 110F | [8 empty] | End user |  | 0
| 1110 | Energy_Storage_Mode_Control | U16 |  |  | 0 | 4 | RW | Energy storage operating mode setting. 0: Self-generating and self-consumption mode 1: time-sharing tariff mode 2: Timed charging and discharging mode 3: Passive mode 4: Peak-shaving mode Used to change the operating mode. | End user | 1 | 65536
| 1111 | Timing_ID | U16 |  |  | 0 | 3 | RW | Timed charging and discharging - rule sequence number. The smaller the serial number, the higher the priority. After successfully writing this register, the timing charge parameter will be updated to the parameter corresponding to the written serial number. | End user | 1 | 131072
| 1112 | Timing_On_Off_Control | U16 |  |  | 0 | 1 | RW | Timed charge/discharge-enable control. Bit0:Charge enable Bit1: Discharge enable | End user | 1 | 262144
| 1113 | Timing_Charge_Start | U16 | 1 1 | hours minutes | 0 0 | 23 59 | RW | High Byte. Charging start hour Low byte. Charge start minute | End user | 1 | 524288
| 1114 | Timing_Charge_End | U16 | 1 1 | hours minutes | 0 0 | 23 59 | RW | High Byte. End of charge hours Low Byte. Charge end minutes | End user | 1 | 1048576
| 1115 | Timing_Discharge_Start | U16 | 1 1 | hours minutes | 0 0 | 23 59 | RW | High Byte. Discharge start hours Low Byte. Discharge start minutes | End user | 1 | 2097152
| 1116 | Timing_Discharge_End | U16 | 1 1 | hours minutes | 0 0 | 23 59 | RW | High Byte. End of discharge hours Low Byte. Discharge end minutes | End user | 1 | 4194304
| 1117 | Timing_Power_Charge | U32 | 1 | W | 1 | 4294967296 | RW | Timed charging and discharging - charging power | End user | 1 | 8388608
| 1118 | [8 empty] | End user | 1 | 16777216
| 1119 | Timing_Power_Discharge | U32 | 1 | W | 1 | 4294967296 | RW | Timed charge/discharge-discharge power | End user | 1 | 33554432
| 111A | [8 empty] | End user | 1 | 67108864
| 111B | Timing_Rsvd1 | [6 empty] | Timed charging and discharging-reserve 1 | End user |  | 0
| 111C | Timing_Rsvd2 | [6 empty] | Timed charging and discharging-reserve 2 | End user |  | 0
| 111D | Timing_Rsvd3 | [6 empty] | Timing charge and discharge-reserve 3 | End user |  | 0
| 111E | Timing_Rsvd4 | [6 empty] | Timing charge and discharge-reserve 4 | End user |  | 0
| 111F | Timing_Control | U16 |  |  | 1 | 1 | RW | Timing charge and discharge write control. (a) When the write value is 1, the value in the Timing Charge shadow register is updated to the system Timing Charge configuration. When reading, the status of the last write operation is returned to 0x0000: success 0x0001: operation in progress 0xFFFB: operation failed, the controller refuses to respond (maybe the controller is busy or configuration error) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, input parameters are wrong | End user | 1 | 2147483648
| 1120 | TOU_ID | U16 |  |  | 0 | 7 | RW | Time-sharing tariff-rule serial number. The smaller the serial number is, the higher the priority is. After successful writing to this register, the time-of-day tariff parameters will be updated to the parameters corresponding to the written serial number. | End user | 1 | 4294967296
| 1121 | TOU_On_Off_Control | U16 |  |  | 0 | 1 | RW | time-of-use tariff-rule enable. 0: Disable 1: enable | End user | 1 | 8589934592
| 1122 | TOU_Charge_Start | U16 | 1 1 | hours minutes | 0 0 | 23 59 | RW | High Byte. Charging start hour Low byte. Charge start minutes | End user | 1 | 17179869184
| 1123 | TOU_Charge_End | U16 | 1 1 | hours minutes | 0 0 | 23 59 | RW | High Byte. End of charge hours Low Byte. Charge end minutes | End user | 1 | 34359738368
| 1124 | TOU_Charge_Target_SOC | U16 | 1 | % | 30 | 100 | RW | Timeshare-Forced Charge Cutoff SOC. The percentage of power remaining, when the current SOC of the battery reaches this register value, the forced charge ends and enters self-generating mode, while discharging is prohibited. | End user | 1 | 68719476736
| 1125 | TOU_Charge_Power | U32 | 1 | W | 1 | 4294967296 | RW | Time-sharing tariff-Forced charging power. The set value cannot exceed the rated power of the machine. | End user | 1 | 137438953472
| 1126 | [8 empty] | End user | 1 | 274877906944
| 1127 | TOU_Executed_Date_Start | U16 | 1 1 | month day | 1 1 | 12 31 | RW | High Byte. Month the rule goes into effect Low Byte. Date the rule became effective | End user | 1 | 549755813888
| 1128 | TOU_Executed_Date_End | U16 | 1 1 | month day | 1 1 | 12 31 | RW | High Byte. Month the rule stopped taking effect Low Byte. The date the rule ceased to be effective | End user | 1 | 1099511627776
| 1129 | TOU_Executed_Day_of_Week | U16 |  |  |  |  | RW | Timeshare-Rule Effective Week. This register is represented by a bit field, bit 0 indicates an invalid week, bit 1 indicates a valid week Bit0：Monday Bit1：Tuesday Bit2：Wednesday Bit3：Thursday Bit4：Friday Bit5: Saturday Bit6: Sunday | End user | 1 | 2199023255552
| 112A | TOU_Rsvd1 | [6 empty] | Time-of-use tariff - Reserved 1 | End user |  | 0
| 112B | TOU_Rsvd2 | [6 empty] | Time Share Tariff - Reserved 2 | End user |  | 0
| 112C | TOU_Rsvd3 | [6 empty] | Time share tariff - reserved 3 | End user |  | 0
| 112D | TOU_Rsvd4 | [6 empty] | Time share tariff-reserve 4 | End user |  | 0
| 112E | TOU_Rsvd5 | [6 empty] | Time share tariff-reserve 5 | End user |  | 0
| 112F | TOU_Control | U16 |  |  | 1 | 1 | RW | Time-of-use tariff - write control. (a) When the write value is 1, the value in the timesharing tariff shadow register is updated to the system timesharing tariff configuration. When read, the status of the last write operation is returned. 0x0000: successful 0x0001: operation in progress 0xFFFB: operation failed, controller refuses to respond (possibly controller is busy or misconfigured) 0xFFFC: operation failed, no response from the controller 0xFFFD: operation failed, current function is disabled 0xFFFE: operation failed, parameter storage failed 0xFFFF: operation failed, input parameters are wrong | End user | 1 | 140737488355328
| 1130 | Peak_Shaving_Discharge_Threshold | U32 | 1 | W | 100 |  | RW | The upper limit of the power allowed to the system to buy power from the grid | End user |  | 0
| 1131 | [8 empty] | End user |  | 0
| 1132 | Peak_Shaving_Charge_Threshold | U32 | 1 | W | 100 |  | RW | Upper limit of the power allowed to the system to sell power to the grid | End user |  | 0
| 1133 | [8 empty] | End user |  | 0
1134
1135
1136
1137
1138
1139
113A
113B
113C
113D
113E
113F
| 1140 | AddressMask_Config_Remote2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above and including the address of this field. bit4 represents the address where the highest bit of the address of this field plus 1 is located. 0 means invalid; 1 means valid. | End user | 00000000 | 0000000F
| 1141 | [8 empty] | End user
| 1142 | [8 empty] | End user
| 1143 | [8 empty] | End user
| 1144 | [9 empty] | 0 | 0
1145
1146
1147
1148
1149
114A
114B
114C
114D
114E
114F
1150
1151
1152
1153
1154
1155
1156
1157
1158
1159
115A
115B
115C
115D
115E
115F
1160
1161
1162
1163
1164
1165
1166
1167
1168
1169
116A
116B
116C
116D
116E
116F
1170
1171
1172
1173
1174
1175
1176
1177
1178
1179
117A
117B
117C
117D
117E
117F
| 1180 | AddressMask_Config_Remote3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid | End user | 00000000 | 00001F8F
| 1181 | [8 empty] | End user
| 1182 | [8 empty] | End user
| 1183 | [8 empty] | End user
| 1184 | Passive_Timeout | U16 | 1 | seconds | 0 | 65535 | RW | Passive mode-timeout control; Default value: 0; Set the passive mode communication timeout time. When the inverter does not receive any communication within the time set by this register, the inverter will force the timeout action. In particular, writing 0 to this register will disable the timeout function | End user | 0 | 0
| 1185 | Passive_Timeout_Action | U16 |  |  | 0 | 1 | RW | Passive mode-timeout action; 0: Forced standby 1: Forced to restore to the energy storage mode before entering the passive mode | End user |  | 0
| 1186 | Passive_Rsvd1 | [7 empty] | End user |  | 0
| 1187 | Passive_Manual_Gdes | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode expected grid power (Gdes); A positive value indicates the power direction "from the grid to the system"; Negative values ​​indicate the power direction "from system to grid | End user | 1 | 128
| 1188 | [8 empty] | End user | 1 | 256
| 1189 | Passive_Manual_Blo | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode expected grid power (Gdes); A positive value indicates the power direction "from the grid to the system"; Negative values ​​indicate the power direction "from system to grid | End user | 1 | 512
| 118A | [8 empty] | End user | 1 | 1024
| 118B | Passive_Manual_Bup | I32 | 1 | W | -2147483648 | 2147483647 | RW | The maximum charge and discharge power of the battery in Manual mode (Bup); Positive value means charging; Negative values ​​indicate discharge | End user | 1 | 2048
| 118C | [8 empty] | End user | 1 | 4096
| 118D | Passive_Manual_Gdzup | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode allows selling electric power (Gdzup); A positive value indicates the power direction "from the grid to the system"; Negative values ​​indicate the power direction "from system to grid Only wirks with peak-shaving mode | End user |  | 0
| 118E | [8 empty] | End user |  | 0
| 118F | Passive_Manual_Gdzlo | I32 | 1 | W | -2147483648 | 2147483647 | RW | Manual mode allows to buy electric power (Gdzlo); A positive value indicates the power direction "from the grid to the system"; Negative values ​​indicate the power direction "from system to grid" Only wirks with peak-shaving mode | End user |  | 0
| 1190 | [8 empty] | End user |  | 0
| 1191 | Passive_Scheduler_Gdes_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode expected grid power (Gdes_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative value means power direction "from system to grid | End user |  | 0
| 1192 | [8 empty] | End user |  | 0
| 1193 | Passive_Scheduler_Blo_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Minimum charge and discharge power of the battery in Scheduler mode (Blo_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values ​​indicate the power direction "from system to grid | End user |  | 0
| 1194 | [8 empty] | End user |  | 0
| 1195 | Passive_Scheduler_Bup_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | The maximum charge and discharge power of the battery in Scheduler mode (Bup_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values ​​indicate the power direction "from system to grid" | End user |  | 0
| 1196 | [8 empty] | End user |  | 0
| 1197 | Passive_Scheduler_Gdzup_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to sell electric power (Gdzup_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values ​​indicate the power direction "from system to grid" | End user |  | 0
| 1198 | [8 empty] | End user |  | 0
| 1199 | Passive_Scheduler_Gdzlo_Ante | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to buy electric power (Gdzlo_Ante); The parameters of the planned task are valid during the planned time period. A positive value indicates the power direction "from the grid to the system"; Negative values ​​indicate the power direction "from system to grid" | End user |  | 0
| 119A | [8 empty] | End user |  | 0
| 119B | Passive_Scheduler_Gdes_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode expected grid power (Gdes_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values ​​indicate the power direction "from system to grid" | End user |  | 0
| 119C | [8 empty] | End user |  | 0
| 119D | Passive_Scheduler_Blo_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | The minimum charge and discharge power of the battery in Scheduler mode (Blo_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values ​​indicate the power direction "from system to grid" | End user |  | 0
| 119E | [8 empty] | End user |  | 0
| 119F | Passive_Scheduler_Bup_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | The maximum charge and discharge power of the battery in Scheduler mode (Bup_Post); Scheduled task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values ​​indicate the power direction "from system to grid". | End user |  | 0
| 11A0 | [8 empty] | End user |  | 0
| 11A1 | Passive_Scheduler_Gdzup_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows selling electric power (Gdzup_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values ​​indicate the power direction "from system to grid" | End user |  | 0
| 11A2 | [8 empty] | End user |  | 0
| 11A3 | Passive_Scheduler_Gdzlo_Post | I32 | 1 | W | -2147483648 | 2147483647 | RW | Scheduler mode allows to buy electric power (Gdzlo_Post); Schedule task parameters, valid after the scheduled time period. A positive value indicates the power direction "from the grid to the system"; Negative values ​​indicate the power direction "from system to grid | End user |  | 0
| 11A4 | [8 empty] | End user |  | 0
| 11A5 | Passive_Scheduler_StartTime | U32 | 1 | seconds | 0 | 4294967296 | RW | Scheduler mode application expected parameter setting value start time; StartTime is in unix time format. Since the internal time of the system defaults to Greenwich Mean Time (GMT), when setting this parameter, you should pay attention to the local time zone of your country, StartTime=(local Unix Time)±(local time and UTC/GMT The number of seconds corresponding to the time difference) | End user |  | 0
| 11A6 | [8 empty] | End user |  | 0
| 11A7 | Passive_Scheduler_DurationTime | U32 | 1 | seconds | 0 | 4294967296 | RW | Scheduler mode application expects the duration of parameter setting value (DurationTime) | End user |  | 0
| 11A8 | [8 empty] | End user |  | 0
| 11A9 | Passive_Scheduler_ManagementMode | U16 |  |  | 0 | 2 | RW | Scheduler mode management mode selection (ManagementMode); 0: Spontaneous self-use mode 1: Manual mode 2: Scheduler mode Only 0, 1, 2 can be input, other data is invalid. | End user |  | 0
11AA
11AB
11AC
11AD
11AE
11AF
11B0
11B1
11B2
11B3
11B4
11B5
11B6
11B7
11B8
11B9
11BA
11BB
11BC
11BD
11BE
11BF
| 11C0 | AddressMask_Config_Remote4 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid. | End user | 00000000 | 0000000F
| 11C1 | [8 empty] | End user
| 11C2 | [8 empty] | End user
| 11C3 | [8 empty] | End user
| 11C4 | [9 empty] | 0 | 0
11C5
The inverter returns a read-only result(0x1300-0x15FF)
| 1300 | AddressMask_Config_ReadOnly_Result1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid |  | 0000000F | FFFFFFFF
1301
1302
1303
| 1304 | Italay_Autotest_Result1 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s1. The default setting of the first-level overvoltage protection value |  | 1 | 16
| 1305 | Italay_Autotest_Result2 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s1. The first-level overvoltage protection time is set by default. |  | 1 | 32
| 1306 | Italay_Autotest_Result3 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s1. Test result of first-level overvoltage protection value. |  | 1 | 64
| 1307 | Italay_Autotest_Result4 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s1. The first level overvoltage protection time test result. |  | 1 | 128
| 1308 | Italay_Autotest_Result5 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s2. The secondary overvoltage protection value is set by default. |  | 1 | 256
| 1309 | Italay_Autotest_Result6 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s2. The secondary overvoltage protection time is set by default |  | 1 | 512
| 130A | Italay_Autotest_Result7 | U16 | 0.1 | V |  |  | R | Italian automatic test 59.s2. Test result of secondary overvoltage protection value. |  | 1 | 1024
| 130B | Italay_Autotest_Result8 | U16 | 1 | ms |  |  | R | Italian automatic test 59.s2. Test result of secondary overvoltage protection time. |  | 1 | 2048
| 130C | Italay_Autotest_Result9 | U16 | 0.1 | V |  |  | R | Italian automatic test 27.s1. The first-level undervoltage protection value is set by default |  | 1 | 4096
| 130D | Italay_Autotest_Result10 | U16 | 1 | ms |  |  | R | "Italian automatic test 27.s1. |  | 1 | 8192
| 130E | Italay_Autotest_Result11 | U16 | 0.1 | V |  |  | R | The first-level undervoltage protection time is set by default. " |  | 1 | 16384
| 130F | Italay_Autotest_Result12 | U16 | 1 | ms |  |  | R | "Italian automatic test 27.s1. |  | 1 | 32768
| 1310 | Italay_Autotest_Result13 | U16 | 0.1 | V |  |  | R | The first level undervoltage protection value test result. " |  | 1 | 65536
| 1311 | Italay_Autotest_Result14 | U16 | 1 | ms |  |  | R | "Italian automatic test 27.s1. |  | 1 | 131072
| 1312 | Italay_Autotest_Result15 | U16 | 0.1 | V |  |  | R | The first level undervoltage protection time test result. " |  | 1 | 262144
| 1313 | Italay_Autotest_Result16 | U16 | 1 | ms |  |  | R | "Italian automatic test 27.s2. |  | 1 | 524288
| 1314 | Italay_Autotest_Result17 | U16 | 0.01 | Hz |  |  | R | The secondary undervoltage protection value is set by default. " |  | 1 | 1048576
| 1315 | Italay_Autotest_Result18 | U16 | 1 | ms |  |  | R | "Italian automatic test 27.s2. |  | 1 | 2097152
| 1316 | Italay_Autotest_Result19 | U16 | 0.01 | Hz |  |  | R | The secondary undervoltage protection time is set by default. " |  | 1 | 4194304
| 1317 | Italay_Autotest_Result20 | U16 | 1 | ms |  |  | R | "Italian automatic test 27.s2. |  | 1 | 8388608
| 1318 | Italay_Autotest_Result21 | U16 | 0.01 | Hz |  |  | R | Test result of secondary undervoltage protection value. " |  | 1 | 16777216
| 1319 | Italay_Autotest_Result22 | U16 | 1 | ms |  |  | R | "Italian automatic test 27.s2. |  | 1 | 33554432
| 131A | Italay_Autotest_Result23 | U16 | 0.01 | Hz |  |  | R | Test result of secondary undervoltage protection time. " |  | 1 | 67108864
| 131B | Italay_Autotest_Result24 | U16 | 1 | ms |  |  | R | "Italian automatic test 81>s1. |  | 1 | 134217728
| 131C | Italay_Autotest_Result25 | U16 | 0.01 | Hz |  |  | R | The first-level over-frequency protection value is set by default. " |  | 1 | 268435456
| 131D | Italay_Autotest_Result26 | U16 | 1 | ms |  |  | R | "Italian automatic test 81>s1. |  | 1 | 536870912
| 131E | Italay_Autotest_Result27 | U16 | 0.01 | Hz |  |  | R | The first-level over-frequency protection time is set by default. " |  | 1 | 1073741824
| 131F | Italay_Autotest_Result28 | U16 | 1 | ms |  |  | R | "Italian automatic test 81>s1. |  | 1 | 2147483648
| 1320 | Italay_Autotest_Result29 | U16 | 0.01 | Hz |  |  | R | Test result of level 1 over-frequency protection value. " |  | 1 | 4294967296
| 1321 | Italay_Autotest_Result30 | U16 | 1 | ms |  |  | R | Italian Auto Test 81<s2. |  | 1 | 8589934592
| 1322 | Italay_Autotest_Result31 | U16 | 0.01 | Hz |  |  | R | The second level under-frequency protection time is set by default. " |  | 1 | 17179869184
| 1323 | Italay_Autotest_Result32 | U16 | 1 | ms |  |  | R | "Italian Auto Test 81<s2. |  | 1 | 34359738368
| 1324 | Italay_Autotest_Result33 | [6 empty] | Test result of secondary underfrequency protection value. " |  |  | 0
| 1325 | Italay_Autotest_Result34 | [6 empty] | "Italian Auto Test 81<s2. |  |  | 0
| 1326 | Italay_Autotest_Result35 | [6 empty] | Test result of secondary under-frequency protection time. " |  |  | 0
| 1327 | Italay_Autotest_Result36 | [6 empty] | Italy automatic test result 36 |  |  | 0
| 1328 | Italay_Autotest_Result37 | [6 empty] | Italy automatic test result 37 |  |  | 0
| 1329 | Italay_Autotest_Result38 | [6 empty] | Italy automatic test result 38 |  |  | 0
| 132A | Italay_Autotest_Result39 | [6 empty] | Italy automatic test result 39 |  |  | 0
| 132B | Italay_Autotest_Result40 | [6 empty] | Italian automatic test result 40 |  |  | 0
| 132C | Italay_Autotest_Result41 | [6 empty] | Italian automatic test result 41 |  |  | 0
| 132D | Italay_Autotest_Result42 | [6 empty] | Italian automatic test result 42 |  |  | 0
| 132E | Italay_Autotest_Result43 | [6 empty] | Italy automatic test result 43 |  |  | 0
| 132F | Italay_Autotest_Result44 | [6 empty] | Italy automatic test result 44 |  |  | 0
| 1330 | Italay_Autotest_Result45 | [6 empty] | Italy automatic test result 45 |  |  | 0
| 1331 | Italay_Autotest_Result46 | [6 empty] | Italy automatic test result 46 |  |  | 0
| 1332 | Italay_Autotest_Result47 | [6 empty] | Italy automatic test result 47 |  |  | 0
| 1333 | Italay_Autotest_Result48 | [6 empty] | Italy automatic test result 48 |  |  | 0
| 1340 | AddressMask_Config_ReadOnly_Result2 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid. |  | FFFFFFFF | FFFFFFFF
1341
1342
1343
| 1344 | IVCurve_Voltage1 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 1 |  | 1 | 16
| 1345 | IVCurve_Current1 | U16 | 0.01 | A |  |  | R | IV curve sweep current 1 |  | 1 | 32
| 1346 | IVCurve_Voltage2 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 2 |  | 1 | 64
| 1347 | IVCurve_Current2 | U16 | 0.01 | A |  |  | R | IV curve scan current 2 |  | 1 | 128
| 1348 | IVCurve_Voltage3 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 3 |  | 1 | 256
| 1349 | IVCurve_Current3 | U16 | 0.01 | A |  |  | R | IV curve scan current 3 |  | 1 | 512
| 134A | IVCurve_Voltage4 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 4 |  | 1 | 1024
| 134B | IVCurve_Current4 | U16 | 0.01 | A |  |  | R | IV curve scan current 4 |  | 1 | 2048
| 134C | IVCurve_Voltage5 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 5 |  | 1 | 4096
| 134D | IVCurve_Current5 | U16 | 0.01 | A |  |  | R | IV curve scan current 5 |  | 1 | 8192
| 134E | IVCurve_Voltage6 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 6 |  | 1 | 16384
| 134F | IVCurve_Current6 | U16 | 0.01 | A |  |  | R | IV curve scan current 6 |  | 1 | 32768
| 1350 | IVCurve_Voltage7 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 7 |  | 1 | 65536
| 1351 | IVCurve_Current7 | U16 | 0.01 | A |  |  | R | IV curve scan current 7 |  | 1 | 131072
| 1352 | IVCurve_Voltage8 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 8 |  | 1 | 262144
| 1353 | IVCurve_Current8 | U16 | 0.01 | A |  |  | R | IV curve scan current 8 |  | 1 | 524288
| 1354 | IVCurve_Voltage9 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 9 |  | 1 | 1048576
| 1355 | IVCurve_Current9 | U16 | 0.01 | A |  |  | R | IV curve sweep current 9 |  | 1 | 2097152
| 1356 | IVCurve_Voltage10 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 10 |  | 1 | 4194304
| 1357 | IVCurve_Current10 | U16 | 0.01 | A |  |  | R | IV curve sweep current 10 |  | 1 | 8388608
| 1358 | IVCurve_Voltage11 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 11 |  | 1 | 16777216
| 1359 | IVCurve_Current11 | U16 | 0.01 | A |  |  | R | IV curve scan current 11 |  | 1 | 33554432
| 135A | IVCurve_Voltage12 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 12 |  | 1 | 67108864
| 135B | IVCurve_Current12 | U16 | 0.01 | A |  |  | R | IV curve scan current 12 |  | 1 | 134217728
| 135C | IVCurve_Voltage13 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 13 |  | 1 | 268435456
| 135D | IVCurve_Current13 | U16 | 0.01 | A |  |  | R | IV curve sweep current 13 |  | 1 | 536870912
| 135E | IVCurve_Voltage14 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 14 |  | 1 | 1073741824
| 135F | IVCurve_Current14 | U16 | 0.01 | A |  |  | R | IV curve scan current 14 |  | 1 | 2147483648
| 1360 | IVCurve_Voltage15 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 15 |  | 1 | 4294967296
| 1361 | IVCurve_Current15 | U16 | 0.01 | A |  |  | R | IV curve scan current 15 |  | 1 | 8589934592
| 1362 | IVCurve_Voltage16 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 16 |  | 1 | 17179869184
| 1363 | IVCurve_Current16 | U16 | 0.01 | A |  |  | R | IV curve scan current 16 |  | 1 | 34359738368
| 1364 | IVCurve_Voltage17 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 17 |  | 1 | 68719476736
| 1365 | IVCurve_Current17 | U16 | 0.01 | A |  |  | R | IV curve scan current 17 |  | 1 | 137438953472
| 1366 | IVCurve_Voltage18 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 18 |  | 1 | 274877906944
| 1367 | IVCurve_Current18 | U16 | 0.01 | A |  |  | R | IV curve scan current 18 |  | 1 | 549755813888
| 1368 | IVCurve_Voltage19 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 19 |  | 1 | 1099511627776
| 1369 | IVCurve_Current19 | U16 | 0.01 | A |  |  | R | IV curve scan current 19 |  | 1 | 2199023255552
| 136A | IVCurve_Voltage20 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 20 |  | 1 | 4398046511104
| 136B | IVCurve_Current20 | U16 | 0.01 | A |  |  | R | IV curve scan current 20 |  | 1 | 8796093022208
| 136C | IVCurve_Voltage21 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 21 |  | 1 | 17592186044416
| 136D | IVCurve_Current21 | U16 | 0.01 | A |  |  | R | IV curve scan current 21 |  | 1 | 35184372088832
| 136E | IVCurve_Voltage22 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 22 |  | 1 | 70368744177664
| 136F | IVCurve_Current22 | U16 | 0.01 | A |  |  | R | IV curve scan current 22 |  | 1 | 140737488355328
| 1370 | IVCurve_Voltage23 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 23 |  | 1 | 281474976710656
| 1371 | IVCurve_Current23 | U16 | 0.01 | A |  |  | R | IV curve scan current 23 |  | 1 | 562949953421312
| 1372 | IVCurve_Voltage24 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 24 |  | 1 | 1125900000000000
| 1373 | IVCurve_Current24 | U16 | 0.01 | A |  |  | R | IV curve scan current 24 |  | 1 | 2251800000000000
| 1374 | IVCurve_Voltage25 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 25 |  | 1 | 4503600000000000
| 1375 | IVCurve_Current25 | U16 | 0.01 | A |  |  | R | IV curve scan current 25 |  | 1 | 9007200000000000
| 1376 | IVCurve_Voltage26 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 26 |  | 1 | 18014400000000000
| 1377 | IVCurve_Current26 | U16 | 0.01 | A |  |  | R | IV curve scan current 26 |  | 1 | 36028800000000000
| 1378 | IVCurve_Voltage27 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 27 |  | 1 | 72057600000000000
| 1379 | IVCurve_Current27 | U16 | 0.01 | A |  |  | R | IV curve scan current 27 |  | 1 | 1.4412e+17
| 137A | IVCurve_Voltage28 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 28 |  | 1 | 2.8823e+17
| 137B | IVCurve_Current28 | U16 | 0.01 | A |  |  | R | IV curve scan current 28 |  | 1 | 5.7646e+17
| 137C | IVCurve_Voltage29 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 29 |  | 1 | 1.1529e+18
| 137D | IVCurve_Current29 | U16 | 0.01 | A |  |  | R | IV curve scan current 29 |  | 1 | 2.3058e+18
| 137E | IVCurve_Voltage30 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 30 |  | 1 | 4.6117e+18
| 137F | IVCurve_Current30 | U16 | 0.01 | A |  |  | R | IV curve scan current 30 |  | 1 | 9.2234e+18
| 1380 | AddressMask_Config_ReadOnly_Result3 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid |  | FFFFFFFF | FFFFFFFF
1381
1382
1383
| 1384 | IVCurve_Voltage31 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 31 |  | 1 | 16
| 1385 | IVCurve_Current31 | U16 | 0.01 | A |  |  | R | IV curve scan current 31 |  | 1 | 32
| 1386 | IVCurve_Voltage32 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 32 |  | 1 | 64
| 1387 | IVCurve_Current32 | U16 | 0.01 | A |  |  | R | IV curve scan current 32 |  | 1 | 128
| 1388 | IVCurve_Voltage33 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 33 |  | 1 | 256
| 1389 | IVCurve_Current33 | U16 | 0.01 | A |  |  | R | IV curve scan current 33 |  | 1 | 512
| 138A | IVCurve_Voltage34 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 34 |  | 1 | 1024
| 138B | IVCurve_Current34 | U16 | 0.01 | A |  |  | R | IV curve scan current 34 |  | 1 | 2048
| 138C | IVCurve_Voltage35 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 35 |  | 1 | 4096
| 138D | IVCurve_Current35 | U16 | 0.01 | A |  |  | R | IV curve scan current 35 |  | 1 | 8192
| 138E | IVCurve_Voltage36 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 36 |  | 1 | 16384
| 138F | IVCurve_Current36 | U16 | 0.01 | A |  |  | R | IV curve scan current 36 |  | 1 | 32768
| 1390 | IVCurve_Voltage37 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 37 |  | 1 | 65536
| 1391 | IVCurve_Current37 | U16 | 0.01 | A |  |  | R | IV curve scan current 37 |  | 1 | 131072
| 1392 | IVCurve_Voltage38 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 38 |  | 1 | 262144
| 1393 | IVCurve_Current38 | U16 | 0.01 | A |  |  | R | IV curve scan current 38 |  | 1 | 524288
| 1394 | IVCurve_Voltage39 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 39 |  | 1 | 1048576
| 1395 | IVCurve_Current39 | U16 | 0.01 | A |  |  | R | IV curve scan current 39 |  | 1 | 2097152
| 1396 | IVCurve_Voltage40 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 40 |  | 1 | 4194304
| 1397 | IVCurve_Current40 | U16 | 0.01 | A |  |  | R | IV curve scan current 40 |  | 1 | 8388608
| 1398 | IVCurve_Voltage41 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 41 |  | 1 | 16777216
| 1399 | IVCurve_Current41 | U16 | 0.01 | A |  |  | R | IV curve scan current 41 |  | 1 | 33554432
| 139A | IVCurve_Voltage42 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 42 |  | 1 | 67108864
| 139B | IVCurve_Current42 | U16 | 0.01 | A |  |  | R | IV curve scan current 42 |  | 1 | 134217728
| 139C | IVCurve_Voltage43 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 43 |  | 1 | 268435456
| 139D | IVCurve_Current43 | U16 | 0.01 | A |  |  | R | IV curve scan current 43 |  | 1 | 536870912
| 139E | IVCurve_Voltage44 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 44 |  | 1 | 1073741824
| 139F | IVCurve_Current44 | U16 | 0.01 | A |  |  | R | IV curve scan current 44 |  | 1 | 2147483648
| 13A0 | IVCurve_Voltage45 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 45 |  | 1 | 4294967296
| 13A1 | IVCurve_Current45 | U16 | 0.01 | A |  |  | R | IV curve scan current 45 |  | 1 | 8589934592
| 13A2 | IVCurve_Voltage46 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 46 |  | 1 | 17179869184
| 13A3 | IVCurve_Current46 | U16 | 0.01 | A |  |  | R | IV curve scan current 46 |  | 1 | 34359738368
| 13A4 | IVCurve_Voltage47 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 47 |  | 1 | 68719476736
| 13A5 | IVCurve_Current47 | U16 | 0.01 | A |  |  | R | IV curve scan current 47 |  | 1 | 137438953472
| 13A6 | IVCurve_Voltage48 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 48 |  | 1 | 274877906944
| 13A7 | IVCurve_Current48 | U16 | 0.01 | A |  |  | R | IV curve scan current 48 |  | 1 | 549755813888
| 13A8 | IVCurve_Voltage49 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 49 |  | 1 | 1099511627776
| 13A9 | IVCurve_Current49 | U16 | 0.01 | A |  |  | R | IV curve scan current 49 |  | 1 | 2199023255552
| 13AA | IVCurve_Voltage50 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 50 |  | 1 | 4398046511104
| 13AB | IVCurve_Current50 | U16 | 0.01 | A |  |  | R | IV curve scan current 50 |  | 1 | 8796093022208
| 13AC | IVCurve_Voltage51 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 51 |  | 1 | 17592186044416
| 13AD | IVCurve_Current51 | U16 | 0.01 | A |  |  | R | IV curve scan current 51 |  | 1 | 35184372088832
| 13AE | IVCurve_Voltage52 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 52 |  | 1 | 70368744177664
| 13AF | IVCurve_Current52 | U16 | 0.01 | A |  |  | R | IV curve scan current 52 |  | 1 | 140737488355328
| 13B0 | IVCurve_Voltage53 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 53 |  | 1 | 281474976710656
| 13B1 | IVCurve_Current53 | U16 | 0.01 | A |  |  | R | IV curve scan current 53 |  | 1 | 562949953421312
| 13B2 | IVCurve_Voltage54 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 54 |  | 1 | 1125900000000000
| 13B3 | IVCurve_Current54 | U16 | 0.01 | A |  |  | R | IV curve scan current 54 |  | 1 | 2251800000000000
| 13B4 | IVCurve_Voltage55 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 55 |  | 1 | 4503600000000000
| 13B5 | IVCurve_Current55 | U16 | 0.01 | A |  |  | R | IV curve scan current 55 |  | 1 | 9007200000000000
| 13B6 | IVCurve_Voltage56 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 56 |  | 1 | 18014400000000000
| 13B7 | IVCurve_Current56 | U16 | 0.01 | A |  |  | R | IV curve scan current 56 |  | 1 | 36028800000000000
| 13B8 | IVCurve_Voltage57 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 57 |  | 1 | 72057600000000000
| 13B9 | IVCurve_Current57 | U16 | 0.01 | A |  |  | R | IV curve scan current 57 |  | 1 | 1.4412e+17
| 13BA | IVCurve_Voltage58 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 58 |  | 1 | 2.8823e+17
| 13BB | IVCurve_Current58 | U16 | 0.01 | A |  |  | R | IV curve scan current 58 |  | 1 | 5.7646e+17
| 13BC | IVCurve_Voltage59 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 59 |  | 1 | 1.1529e+18
| 13BD | IVCurve_Current59 | U16 | 0.01 | A |  |  | R | IV curve scan current 59 |  | 1 | 2.3058e+18
| 13BE | IVCurve_Voltage60 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 60 |  | 1 | 4.6117e+18
| 13BF | IVCurve_Current60 | U16 | 0.01 | A |  |  | R | IV curve scan current 60 |  | 1 | 9.2234e+18
| 13C0 | AddressMask_Config_ReadOnly_Result4 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid |  | 00000FFF | FFFFFFFF
13C1
13C2
13C3
| 13C4 | IVCurve_Voltage61 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 61 |  | 1 | 16
| 13C5 | IVCurve_Current61 | U16 | 0.01 | A |  |  | R | IV curve scan current 61 |  | 1 | 32
| 13C6 | IVCurve_Voltage62 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 62 |  | 1 | 64
| 13C7 | IVCurve_Current62 | U16 | 0.01 | A |  |  | R | IV curve scan current 62 |  | 1 | 128
| 13C8 | IVCurve_Voltage63 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 63 |  | 1 | 256
| 13C9 | IVCurve_Current63 | U16 | 0.01 | A |  |  | R | IV curve scan current 63 |  | 1 | 512
| 13CA | IVCurve_Voltage64 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 64 |  | 1 | 1024
| 13CB | IVCurve_Current64 | U16 | 0.01 | A |  |  | R | IV curve scan current 64 |  | 1 | 2048
| 13CC | IVCurve_Voltage65 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 65 |  | 1 | 4096
| 13CD | IVCurve_Current65 | U16 | 0.01 | A |  |  | R | IV curve scan current 65 |  | 1 | 8192
| 13CE | IVCurve_Voltage66 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 66 |  | 1 | 16384
| 13CF | IVCurve_Current66 | U16 | 0.01 | A |  |  | R | IV curve scan current 66 |  | 1 | 32768
| 13D0 | IVCurve_Voltage67 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 67 |  | 1 | 65536
| 13D1 | IVCurve_Current67 | U16 | 0.01 | A |  |  | R | IV curve scan current 67 |  | 1 | 131072
| 13D2 | IVCurve_Voltage68 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 68 |  | 1 | 262144
| 13D3 | IVCurve_Current68 | U16 | 0.01 | A |  |  | R | IV curve scan current 68 |  | 1 | 524288
| 13D4 | IVCurve_Voltage69 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 69 |  | 1 | 1048576
| 13D5 | IVCurve_Current69 | U16 | 0.01 | A |  |  | R | IV curve scan current 69 |  | 1 | 2097152
| 13D6 | IVCurve_Voltage70 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 70 |  | 1 | 4194304
| 13D7 | IVCurve_Current70 | U16 | 0.01 | A |  |  | R | IV curve scan current 70 |  | 1 | 8388608
| 13D8 | IVCurve_Voltage71 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 71 |  | 1 | 16777216
| 13D9 | IVCurve_Current71 | U16 | 0.01 | A |  |  | R | IV curve scan current 71 |  | 1 | 33554432
| 13DA | IVCurve_Voltage72 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 72 |  | 1 | 67108864
| 13DB | IVCurve_Current72 | U16 | 0.01 | A |  |  | R | IV curve scan current 72 |  | 1 | 134217728
| 13DC | IVCurve_Voltage73 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 73 |  | 1 | 268435456
| 13DD | IVCurve_Current73 | U16 | 0.01 | A |  |  | R | IV curve scan current 73 |  | 1 | 536870912
| 13DE | IVCurve_Voltage74 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 74 |  | 1 | 1073741824
| 13DF | IVCurve_Current74 | U16 | 0.01 | A |  |  | R | IV curve scan current 74 |  | 1 | 2147483648
| 13E0 | IVCurve_Voltage75 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 75 |  | 1 | 4294967296
| 13E1 | IVCurve_Current75 | U16 | 0.01 | A |  |  | R | IV curve scan current 75 |  | 1 | 8589934592
| 13E2 | IVCurve_Voltage76 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 76 |  | 1 | 17179869184
| 13E3 | IVCurve_Current76 | U16 | 0.01 | A |  |  | R | IV curve scan current 76 |  | 1 | 34359738368
| 13E4 | IVCurve_Voltage77 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 77 |  | 1 | 68719476736
| 13E5 | IVCurve_Current77 | U16 | 0.01 | A |  |  | R | IV curve scan current 77 |  | 1 | 137438953472
| 13E6 | IVCurve_Voltage78 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 78 |  | 1 | 274877906944
| 13E7 | IVCurve_Current78 | U16 | 0.01 | A |  |  | R | IV curve sweep current 78 |  | 1 | 549755813888
| 13E8 | IVCurve_Voltage79 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 79 |  | 1 | 1099511627776
| 13E9 | IVCurve_Current79 | U16 | 0.01 | A |  |  | R | IV curve sweep current 79 |  | 1 | 2199023255552
| 13EA | IVCurve_Voltage80 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 80 |  | 1 | 4398046511104
| 13EB | IVCurve_Current80 | U16 | 0.01 | A |  |  | R | IV curve sweep current 80 |  | 1 | 8796093022208
| 13EC | IVCurve_Voltage81 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 81 |  |  | 0
| 13ED | IVCurve_Current81 | U16 | 0.01 | A |  |  | R | IV curve sweep current 81 |  |  | 0
| 13EE | IVCurve_Voltage82 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 82 |  |  | 0
| 13EF | IVCurve_Current82 | U16 | 0.01 | A |  |  | R | IV curve scan current 82 |  |  | 0
| 13F0 | IVCurve_Voltage83 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 83 |  |  | 0
| 13F1 | IVCurve_Current83 | U16 | 0.01 | A |  |  | R | IV curve sweep current 83 |  |  | 0
| 13F2 | IVCurve_Voltage84 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 84 |  |  | 0
| 13F3 | IVCurve_Current84 | U16 | 0.01 | A |  |  | R | IV curve sweep current 84 |  |  | 0
| 13F4 | IVCurve_Voltage85 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 85 |  |  | 0
| 13F5 | IVCurve_Current85 | U16 | 0.01 | A |  |  | R | IV curve sweep current 85 |  |  | 0
| 13F6 | IVCurve_Voltage86 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 86 |  |  | 0
| 13F7 | IVCurve_Current86 | U16 | 0.01 | A |  |  | R | IV curve scan current 86 |  |  | 0
| 13F8 | IVCurve_Voltage87 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 87 |  |  | 0
| 13F9 | IVCurve_Current87 | U16 | 0.01 | A |  |  | R | IV curve scan current 87 |  |  | 0
| 13FA | IVCurve_Voltage88 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 88 |  |  | 0
| 13FB | IVCurve_Current88 | U16 | 0.01 | A |  |  | R | IV curve sweep current 88 |  |  | 0
| 13FC | IVCurve_Voltage89 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 89 |  |  | 0
| 13FD | IVCurve_Current89 | U16 | 0.01 | A |  |  | R | IV curve scan current 89 |  |  | 0
| 13FE | IVCurve_Voltage90 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 90 |  |  | 0
| 13FF | IVCurve_Current90 | U16 | 0.01 | A |  |  | R | IV curve sweep current 90 |  |  | 0
| 1400 | AddressMask_Config_ReadOnly_Result5 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid. |  | 00000000 | 0000000F
1401
1402
1403
| 1404 | IVCurve_Voltage91 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 91 |  | 0 | 0
| 1405 | IVCurve_Current91 | U16 | 0.01 | A |  |  | R | IV curve sweep current 91 |  |  | 0
| 1406 | IVCurve_Voltage92 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 92 |  |  | 0
| 1407 | IVCurve_Current92 | U16 | 0.01 | A |  |  | R | IV curve scan current 92 |  |  | 0
| 1408 | IVCurve_Voltage93 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 93 |  |  | 0
| 1409 | IVCurve_Current93 | U16 | 0.01 | A |  |  | R | IV curve sweep current 93 |  |  | 0
| 140A | IVCurve_Voltage94 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 94 |  |  | 0
| 140B | IVCurve_Current94 | U16 | 0.01 | A |  |  | R | IV curve scan current 94 |  |  | 0
| 140C | IVCurve_Voltage95 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 95 |  |  | 0
| 140D | IVCurve_Current95 | U16 | 0.01 | A |  |  | R | IV curve sweep current 95 |  |  | 0
| 140E | IVCurve_Voltage96 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 96 |  |  | 0
| 140F | IVCurve_Current96 | U16 | 0.01 | A |  |  | R | IV curve scan current 96 |  |  | 0
| 1410 | IVCurve_Voltage97 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 97 |  |  | 0
| 1411 | IVCurve_Current97 | U16 | 0.01 | A |  |  | R | IV curve scan current 97 |  |  | 0
| 1412 | IVCurve_Voltage98 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 98 |  |  | 0
| 1413 | IVCurve_Current98 | U16 | 0.01 | A |  |  | R | IV curve scan current 98 |  |  | 0
| 1414 | IVCurve_Voltage99 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 99 |  |  | 0
| 1415 | IVCurve_Current99 | U16 | 0.01 | A |  |  | R | IV curve sweep current 99 |  |  | 0
| 1416 | IVCurve_Voltage100 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 100 |  |  | 0
| 1417 | IVCurve_Current100 | U16 | 0.01 | A |  |  | R | IV curve sweep current 100 |  |  | 0
| 1418 | IVCurve_Voltage101 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 101 |  |  | 0
| 1419 | IVCurve_Current101 | U16 | 0.01 | A |  |  | R | IV curve sweep current 101 |  |  | 0
| 141A | IVCurve_Voltage102 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 102 |  |  | 0
| 141B | IVCurve_Current102 | U16 | 0.01 | A |  |  | R | IV curve scan current 102 |  |  | 0
| 141C | IVCurve_Voltage103 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 103 |  |  | 0
| 141D | IVCurve_Current103 | U16 | 0.01 | A |  |  | R | IV curve scan current 103 |  |  | 0
| 141E | IVCurve_Voltage104 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 104 |  |  | 0
| 141F | IVCurve_Current104 | U16 | 0.01 | A |  |  | R | IV curve scan current 104 |  |  | 0
| 1420 | IVCurve_Voltage105 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 105 |  |  | 0
| 1421 | IVCurve_Current105 | U16 | 0.01 | A |  |  | R | IV curve scan current 105 |  |  | 0
| 1422 | IVCurve_Voltage106 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 106 |  |  | 0
| 1423 | IVCurve_Current106 | U16 | 0.01 | A |  |  | R | IV curve scan current 106 |  |  | 0
| 1424 | IVCurve_Voltage107 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 107 |  |  | 0
| 1425 | IVCurve_Current107 | U16 | 0.01 | A |  |  | R | IV curve scan current 107 |  |  | 0
| 1426 | IVCurve_Voltage108 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 108 |  |  | 0
| 1427 | IVCurve_Current108 | U16 | 0.01 | A |  |  | R | IV curve sweep current 108 |  |  | 0
| 1428 | IVCurve_Voltage109 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 109 |  |  | 0
| 1429 | IVCurve_Current109 | U16 | 0.01 | A |  |  | R | IV curve scan current 109 |  |  | 0
| 142A | IVCurve_Voltage110 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 110 |  |  | 0
| 142B | IVCurve_Current110 | U16 | 0.01 | A |  |  | R | IV curve scan current 110 |  |  | 0
| 142C | IVCurve_Voltage111 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 111 |  |  | 0
| 142D | IVCurve_Current111 | U16 | 0.01 | A |  |  | R | IV curve scan current 111 |  |  | 0
| 142E | IVCurve_Voltage112 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 112 |  |  | 0
| 142F | IVCurve_Current112 | U16 | 0.01 | A |  |  | R | IV curve scan current 112 |  |  | 0
| 1430 | IVCurve_Voltage113 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 113 |  |  | 0
| 1431 | IVCurve_Current113 | U16 | 0.01 | A |  |  | R | IV curve scan current 113 |  |  | 0
| 1432 | IVCurve_Voltage114 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 114 |  |  | 0
| 1433 | IVCurve_Current114 | U16 | 0.01 | A |  |  | R | IV curve sweep current 114 |  |  | 0
| 1434 | IVCurve_Voltage115 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 115 |  |  | 0
| 1435 | IVCurve_Current115 | U16 | 0.01 | A |  |  | R | IV curve sweep current 115 |  |  | 0
| 1436 | IVCurve_Voltage116 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 116 |  |  | 0
| 1437 | IVCurve_Current116 | U16 | 0.01 | A |  |  | R | IV curve scan current 116 |  |  | 0
| 1438 | IVCurve_Voltage117 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 117 |  |  | 0
| 1439 | IVCurve_Current117 | U16 | 0.01 | A |  |  | R | IV curve scan current 117 |  |  | 0
| 143A | IVCurve_Voltage118 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 118 |  |  | 0
| 143B | IVCurve_Current118 | U16 | 0.01 | A |  |  | R | IV curve scan current 118 |  |  | 0
| 143C | IVCurve_Voltage119 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 119 |  |  | 0
| 143D | IVCurve_Current119 | U16 | 0.01 | A |  |  | R | IV curve scan current 119 |  |  | 0
| 143E | IVCurve_Voltage120 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 120 |  |  | 0
| 143F | IVCurve_Current120 | U16 | 0.01 | A |  |  | R | IV curve sweep current 120 |  |  | 0
| 1440 | AddressMask_Config_ReadOnly_Result6 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid. |  | 00000000 | 0000000F
1441
1442
1443
| 1444 | IVCurve_Voltage121 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 121 |  | 0 | 0
| 1445 | IVCurve_Current121 | U16 | 0.01 | A |  |  | R | IV curve scan current 121 |  |  | 0
| 1446 | IVCurve_Voltage122 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 122 |  |  | 0
| 1447 | IVCurve_Current122 | U16 | 0.01 | A |  |  | R | IV curve scan current 122 |  |  | 0
| 1448 | IVCurve_Voltage123 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 123 |  |  | 0
| 1449 | IVCurve_Current123 | U16 | 0.01 | A |  |  | R | IV curve scan current 123 |  |  | 0
| 144A | IVCurve_Voltage124 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 124 |  |  | 0
| 144B | IVCurve_Current124 | U16 | 0.01 | A |  |  | R | IV curve scan current 124 |  |  | 0
| 144C | IVCurve_Voltage125 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 125 |  |  | 0
| 144D | IVCurve_Current125 | U16 | 0.01 | A |  |  | R | IV curve sweep current 125 |  |  | 0
| 144E | IVCurve_Voltage126 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 126 |  |  | 0
| 144F | IVCurve_Current126 | U16 | 0.01 | A |  |  | R | IV curve scan current 126 |  |  | 0
| 1450 | IVCurve_Voltage127 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 127 |  |  | 0
| 1451 | IVCurve_Current127 | U16 | 0.01 | A |  |  | R | IV curve scan current 127 |  |  | 0
| 1452 | IVCurve_Voltage128 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 128 |  |  | 0
| 1453 | IVCurve_Current128 | U16 | 0.01 | A |  |  | R | IV curve scan current 128 |  |  | 0
| 1454 | IVCurve_Voltage129 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 129 |  |  | 0
| 1455 | IVCurve_Current129 | U16 | 0.01 | A |  |  | R | IV curve scan current 129 |  |  | 0
| 1456 | IVCurve_Voltage130 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 130 |  |  | 0
| 1457 | IVCurve_Current130 | U16 | 0.01 | A |  |  | R | IV curve scan current 130 |  |  | 0
| 1458 | IVCurve_Voltage131 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 131 |  |  | 0
| 1459 | IVCurve_Current131 | U16 | 0.01 | A |  |  | R | IV curve scan current 131 |  |  | 0
| 145A | IVCurve_Voltage132 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 132 |  |  | 0
| 145B | IVCurve_Current132 | U16 | 0.01 | A |  |  | R | IV curve scan current 132 |  |  | 0
| 145C | IVCurve_Voltage133 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 133 |  |  | 0
| 145D | IVCurve_Current133 | U16 | 0.01 | A |  |  | R | IV curve scan current 133 |  |  | 0
| 145E | IVCurve_Voltage134 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 134 |  |  | 0
| 145F | IVCurve_Current134 | U16 | 0.01 | A |  |  | R | IV curve scan current 134 |  |  | 0
| 1460 | IVCurve_Voltage135 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 135 |  |  | 0
| 1461 | IVCurve_Current135 | U16 | 0.01 | A |  |  | R | IV curve scan current 135 |  |  | 0
| 1462 | IVCurve_Voltage136 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 136 |  |  | 0
| 1463 | IVCurve_Current136 | U16 | 0.01 | A |  |  | R | IV curve scan current 136 |  |  | 0
| 1464 | IVCurve_Voltage137 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 137 |  |  | 0
| 1465 | IVCurve_Current137 | U16 | 0.01 | A |  |  | R | IV curve scan current 137 |  |  | 0
| 1466 | IVCurve_Voltage138 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 138 |  |  | 0
| 1467 | IVCurve_Current138 | U16 | 0.01 | A |  |  | R | IV curve scan current 138 |  |  | 0
| 1468 | IVCurve_Voltage139 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 139 |  |  | 0
| 1469 | IVCurve_Current139 | U16 | 0.01 | A |  |  | R | IV curve scan current 139 |  |  | 0
| 146A | IVCurve_Voltage140 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 140 |  |  | 0
| 146B | IVCurve_Current140 | U16 | 0.01 | A |  |  | R | IV curve sweep current 140 |  |  | 0
| 146C | IVCurve_Voltage141 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 141 |  |  | 0
| 146D | IVCurve_Current141 | U16 | 0.01 | A |  |  | R | IV curve scan current 141 |  |  | 0
| 146E | IVCurve_Voltage142 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 142 |  |  | 0
| 146F | IVCurve_Current142 | U16 | 0.01 | A |  |  | R | IV curve scan current 142 |  |  | 0
| 1470 | IVCurve_Voltage143 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 143 |  |  | 0
| 1471 | IVCurve_Current143 | U16 | 0.01 | A |  |  | R | IV curve scan current 143 |  |  | 0
| 1472 | IVCurve_Voltage144 | U16 | 0.1 | V |  |  | R | IV curve scan voltage 144 |  |  | 0
| 1473 | IVCurve_Current144 | U16 | 0.01 | A |  |  | R | IV curve scan current 144 |  |  | 0
| 1474 | IVCurve_Voltage145 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 145 |  |  | 0
| 1475 | IVCurve_Current145 | U16 | 0.01 | A |  |  | R | IV curve scan current 145 |  |  | 0
| 1476 | IVCurve_Voltage146 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 146 |  |  | 0
| 1477 | IVCurve_Current146 | U16 | 0.01 | A |  |  | R | IV curve scan current 146 |  |  | 0
| 1478 | IVCurve_Voltage147 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 147 |  |  | 0
| 1479 | IVCurve_Current147 | U16 | 0.01 | A |  |  | R | IV curve scan current 147 |  |  | 0
| 147A | IVCurve_Voltage148 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 148 |  |  | 0
| 147B | IVCurve_Current148 | U16 | 0.01 | A |  |  | R | IV curve scan current 148 |  |  | 0
| 147C | IVCurve_Voltage149 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 149 |  |  | 0
| 147D | IVCurve_Current149 | U16 | 0.01 | A |  |  | R | IV curve scan current 149 |  |  | 0
| 147E | IVCurve_Voltage150 | U16 | 0.1 | V |  |  | R | IV curve sweep voltage 150 |  |  | 0
| 147F | IVCurve_Current150 | U16 | 0.01 | A |  |  | R | IV curve scan current 150 |  |  | 0
| 1480 | HistoryEventList_ID1 | U16 |  |  |  |  | R | The latest 1st item of historical event ID
| 1481 | HistoryEventList_yM1 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1482 | HistoryEventList_dH1 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1483 | HistoryEventList_ms1 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1484 | HistoryEventList_ID2 | U16 |  |  |  |  | R | The 2nd most recent historical event ID
| 1485 | HistoryEventList_yM2 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1486 | HistoryEventList_dH2 | U16 |  |  |  |  | R | High byte: date; Low byte: hour. "
| 1487 | HistoryEventList_ms2 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1488 | HistoryEventList_ID3 | U16 |  |  |  |  | R | The 3rd most recent historical event ID
| 1489 | HistoryEventList_yM3 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 148A | HistoryEventList_dH3 | U16 |  |  |  |  | R | High byte: date; Low byte: hour. "
| 148B | HistoryEventList_ms3 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 148C | HistoryEventList_ID4 | U16 |  |  |  |  | R | The 4th most recent historical event ID
| 148D | HistoryEventList_yM4 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 148E | HistoryEventList_dH4 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 148F | HistoryEventList_ms4 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1490 | HistoryEventList_ID5 | U16 |  |  |  |  | R | The 5th most recent historical event ID
| 1491 | HistoryEventList_yM5 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1492 | HistoryEventList_dH5 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1493 | HistoryEventList_ms5 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1494 | HistoryEventList_ID6 | U16 |  |  |  |  | R | The 6th most recent historical event ID
| 1495 | HistoryEventList_yM6 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1496 | HistoryEventList_dH6 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1497 | HistoryEventList_ms6 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1498 | HistoryEventList_ID7 | U16 |  |  |  |  | R | The 7th most recent historical event ID
| 1499 | HistoryEventList_yM7 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 149A | HistoryEventList_dH7 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 149B | HistoryEventList_ms7 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 149C | HistoryEventList_ID8 | U16 |  |  |  |  | R | The 8th most recent historical event ID
| 149D | HistoryEventList_yM8 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 149E | HistoryEventList_dH8 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 149F | HistoryEventList_ms8 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14A0 | HistoryEventList_ID9 | U16 |  |  |  |  | R | The 9th most recent historical event ID
| 14A1 | HistoryEventList_yM9 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14A2 | HistoryEventList_dH9 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14A3 | HistoryEventList_ms9 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14A4 | HistoryEventList_ID10 | U16 |  |  |  |  | R | The 10th most recent historical event ID
| 14A5 | HistoryEventList_yM10 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14A6 | HistoryEventList_dH10 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14A7 | HistoryEventList_ms10 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14A8 | HistoryEventList_ID11 | U16 |  |  |  |  | R | The 11th most recent historical event ID
| 14A9 | HistoryEventList_yM11 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14AA | HistoryEventList_dH11 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14AB | HistoryEventList_ms11 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14AC | HistoryEventList_ID12 | U16 |  |  |  |  | R | The 12th most recent historical event ID
| 14AD | HistoryEventList_yM12 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14AE | HistoryEventList_dH12 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14AF | HistoryEventList_ms12 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14B0 | HistoryEventList_ID13 | U16 |  |  |  |  | R | The 13th most recent historical event ID
| 14B1 | HistoryEventList_yM13 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14B2 | HistoryEventList_dH13 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14B3 | HistoryEventList_ms13 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14B4 | HistoryEventList_ID14 | U16 |  |  |  |  | R | The 14th most recent historical event ID
| 14B5 | HistoryEventList_yM14 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14B6 | HistoryEventList_dH14 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14B7 | HistoryEventList_ms14 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14B8 | HistoryEventList_ID15 | U16 |  |  |  |  | R | The 15th most recent historical event ID
| 14B9 | HistoryEventList_yM15 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14BA | HistoryEventList_dH15 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14BB | HistoryEventList_ms15 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14BC | HistoryEventList_ID16 | U16 |  |  |  |  | R | The 16th most recent historical event ID
| 14BD | HistoryEventList_yM16 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14BE | HistoryEventList_dH16 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14BF | HistoryEventList_ms16 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14C0 | HistoryEventList_ID17 | U16 |  |  |  |  | R | The 17th most recent historical event ID
| 14C1 | HistoryEventList_yM17 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14C2 | HistoryEventList_dH17 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14C3 | HistoryEventList_ms17 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14C4 | HistoryEventList_ID18 | U16 |  |  |  |  | R | The 18th most recent historical event ID
| 14C5 | HistoryEventList_yM18 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14C6 | HistoryEventList_dH18 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14C7 | HistoryEventList_ms18 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14C8 | HistoryEventList_ID19 | U16 |  |  |  |  | R | The 19th most recent historical event ID
| 14C9 | HistoryEventList_yM19 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14CA | HistoryEventList_dH19 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14CB | HistoryEventList_ms19 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14CC | HistoryEventList_ID20 | U16 |  |  |  |  | R | The 20th most recent historical event ID
| 14CD | HistoryEventList_yM20 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14CE | HistoryEventList_dH20 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14CF | HistoryEventList_ms20 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14D0 | HistoryEventList_ID21 | U16 |  |  |  |  | R | The 21th most recent historical event ID
| 14D1 | HistoryEventList_yM21 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14D2 | HistoryEventList_dH21 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14D3 | HistoryEventList_ms21 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14D4 | HistoryEventList_ID22 | U16 |  |  |  |  | R | The 22th most recent historical event ID
| 14D5 | HistoryEventList_yM22 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14D6 | HistoryEventList_dH22 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14D7 | HistoryEventList_ms22 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14D8 | HistoryEventList_ID23 | U16 |  |  |  |  | R | The 23th most recent historical event ID
| 14D9 | HistoryEventList_yM23 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14DA | HistoryEventList_dH23 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14DB | HistoryEventList_ms23 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14DC | HistoryEventList_ID24 | U16 |  |  |  |  | R | The 24th most recent historical event ID
| 14DD | HistoryEventList_yM24 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14DE | HistoryEventList_dH24 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14DF | HistoryEventList_ms24 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14E0 | HistoryEventList_ID25 | U16 |  |  |  |  | R | The 25th most recent historical event ID
| 14E1 | HistoryEventList_yM25 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14E2 | HistoryEventList_dH25 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14E3 | HistoryEventList_ms25 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14E4 | HistoryEventList_ID26 | U16 |  |  |  |  | R | The 26th most recent historical event ID
| 14E5 | HistoryEventList_yM26 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14E6 | HistoryEventList_dH26 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14E7 | HistoryEventList_ms26 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14E8 | HistoryEventList_ID27 | U16 |  |  |  |  | R | The 27th most recent historical event ID
| 14E9 | HistoryEventList_yM27 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14EA | HistoryEventList_dH27 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14EB | HistoryEventList_ms27 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14EC | HistoryEventList_ID28 | U16 |  |  |  |  | R | The 28th most recent historical event ID
| 14ED | HistoryEventList_yM28 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14EE | HistoryEventList_dH28 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14EF | HistoryEventList_ms28 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14F0 | HistoryEventList_ID29 | U16 |  |  |  |  | R | The 29th most recent historical event ID
| 14F1 | HistoryEventList_yM29 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14F2 | HistoryEventList_dH29 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14F3 | HistoryEventList_ms29 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14F4 | HistoryEventList_ID30 | U16 |  |  |  |  | R | The 30th most recent historical event ID
| 14F5 | HistoryEventList_yM30 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14F6 | HistoryEventList_dH30 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14F7 | HistoryEventList_ms30 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14F8 | HistoryEventList_ID31 | U16 |  |  |  |  | R | The 31th most recent historical event ID
| 14F9 | HistoryEventList_yM31 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14FA | HistoryEventList_dH31 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14FB | HistoryEventList_ms31 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 14FC | HistoryEventList_ID32 | U16 |  |  |  |  | R | The 32th most recent historical event ID
| 14FD | HistoryEventList_yM32 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 14FE | HistoryEventList_dH32 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 14FF | HistoryEventList_ms32 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1500 | HistoryEventList_ID33 | U16 |  |  |  |  | R | The 33th most recent historical event ID
| 1501 | HistoryEventList_yM33 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1502 | HistoryEventList_dH33 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1503 | HistoryEventList_ms33 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1504 | HistoryEventList_ID34 | U16 |  |  |  |  | R | The 34th most recent historical event ID
| 1505 | HistoryEventList_yM34 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1506 | HistoryEventList_dH34 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1507 | HistoryEventList_ms34 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1508 | HistoryEventList_ID35 | U16 |  |  |  |  | R | The 35th most recent historical event ID
| 1509 | HistoryEventList_yM35 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 150A | HistoryEventList_dH35 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 150B | HistoryEventList_ms35 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 150C | HistoryEventList_ID36 | U16 |  |  |  |  | R | The 36th most recent historical event ID
| 150D | HistoryEventList_yM36 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 150E | HistoryEventList_dH36 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 150F | HistoryEventList_ms36 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1510 | HistoryEventList_ID37 | U16 |  |  |  |  | R | The 37th most recent historical event ID
| 1511 | HistoryEventList_yM37 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1512 | HistoryEventList_dH37 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1513 | HistoryEventList_ms37 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1514 | HistoryEventList_ID38 | U16 |  |  |  |  | R | The 38th most recent historical event ID
| 1515 | HistoryEventList_yM38 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1516 | HistoryEventList_dH38 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1517 | HistoryEventList_ms38 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1518 | HistoryEventList_ID39 | U16 |  |  |  |  | R | The 39th most recent historical event ID
| 1519 | HistoryEventList_yM39 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 151A | HistoryEventList_dH39 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 151B | HistoryEventList_ms39 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 151C | HistoryEventList_ID40 | U16 |  |  |  |  | R | The 40th most recent historical event ID
| 151D | HistoryEventList_yM40 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 151E | HistoryEventList_dH40 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 151F | HistoryEventList_ms40 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1520 | HistoryEventList_ID41 | U16 |  |  |  |  | R | The 41th most recent historical event ID
| 1521 | HistoryEventList_yM41 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1522 | HistoryEventList_dH41 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1523 | HistoryEventList_ms41 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1524 | HistoryEventList_ID42 | U16 |  |  |  |  | R | The 42th most recent historical event ID
| 1525 | HistoryEventList_yM42 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1526 | HistoryEventList_dH42 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1527 | HistoryEventList_ms42 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1528 | HistoryEventList_ID43 | U16 |  |  |  |  | R | The 43th most recent historical event ID
| 1529 | HistoryEventList_yM43 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 152A | HistoryEventList_dH43 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 152B | HistoryEventList_ms43 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 152C | HistoryEventList_ID44 | U16 |  |  |  |  | R | The 44th most recent historical event ID
| 152D | HistoryEventList_yM44 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 152E | HistoryEventList_dH44 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 152F | HistoryEventList_ms44 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1530 | HistoryEventList_ID45 | U16 |  |  |  |  | R | The 45th most recent historical event ID
| 1531 | HistoryEventList_yM45 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1532 | HistoryEventList_dH45 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1533 | HistoryEventList_ms45 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1534 | HistoryEventList_ID46 | U16 |  |  |  |  | R | The 46th most recent historical event ID
| 1535 | HistoryEventList_yM46 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1536 | HistoryEventList_dH46 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1537 | HistoryEventList_ms46 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1538 | HistoryEventList_ID47 | U16 |  |  |  |  | R | The 47th most recent historical event ID
| 1539 | HistoryEventList_yM47 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 153A | HistoryEventList_dH47 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 153B | HistoryEventList_ms47 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 153C | HistoryEventList_ID48 | U16 |  |  |  |  | R | The 48th most recent historical event ID
| 153D | HistoryEventList_yM48 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 153E | HistoryEventList_dH48 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 153F | HistoryEventList_ms48 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1540 | HistoryEventList_ID49 | U16 |  |  |  |  | R | The 49th most recent historical event ID
| 1541 | HistoryEventList_yM49 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1542 | HistoryEventList_dH49 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1543 | HistoryEventList_ms49 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1544 | HistoryEventList_ID50 | U16 |  |  |  |  | R | The 50th most recent historical event ID
| 1545 | HistoryEventList_yM50 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1546 | HistoryEventList_dH50 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1547 | HistoryEventList_ms50 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1548 | HistoryEventList_ID51 | U16 |  |  |  |  | R | The 51th most recent historical event ID
| 1549 | HistoryEventList_yM51 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 154A | HistoryEventList_dH51 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 154B | HistoryEventList_ms51 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 154C | HistoryEventList_ID52 | U16 |  |  |  |  | R | The 52th most recent historical event ID
| 154D | HistoryEventList_yM52 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 154E | HistoryEventList_dH52 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 154F | HistoryEventList_ms52 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1550 | HistoryEventList_ID53 | U16 |  |  |  |  | R | The 53th most recent historical event ID
| 1551 | HistoryEventList_yM53 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1552 | HistoryEventList_dH53 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1553 | HistoryEventList_ms53 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1554 | HistoryEventList_ID54 | U16 |  |  |  |  | R | The 54th most recent historical event ID
| 1555 | HistoryEventList_yM54 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1556 | HistoryEventList_dH54 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1557 | HistoryEventList_ms54 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1558 | HistoryEventList_ID55 | U16 |  |  |  |  | R | The 55th most recent historical event ID
| 1559 | HistoryEventList_yM55 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 155A | HistoryEventList_dH55 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 155B | HistoryEventList_ms55 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 155C | HistoryEventList_ID56 | U16 |  |  |  |  | R | The 56th most recent historical event ID
| 155D | HistoryEventList_yM56 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 155E | HistoryEventList_dH56 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 155F | HistoryEventList_ms56 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1560 | HistoryEventList_ID57 | U16 |  |  |  |  | R | The 57th most recent historical event ID
| 1561 | HistoryEventList_yM57 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1562 | HistoryEventList_dH57 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1563 | HistoryEventList_ms57 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1564 | HistoryEventList_ID58 | U16 |  |  |  |  | R | The 58th most recent historical event ID
| 1565 | HistoryEventList_yM58 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1566 | HistoryEventList_dH58 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1567 | HistoryEventList_ms58 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1568 | HistoryEventList_ID59 | U16 |  |  |  |  | R | The 59th most recent historical event ID
| 1569 | HistoryEventList_yM59 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 156A | HistoryEventList_dH59 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 156B | HistoryEventList_ms59 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 156C | HistoryEventList_ID60 | U16 |  |  |  |  | R | The 60th most recent historical event ID
| 156D | HistoryEventList_yM60 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 156E | HistoryEventList_dH60 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 156F | HistoryEventList_ms60 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1570 | HistoryEventList_ID61 | U16 |  |  |  |  | R | The 61th most recent historical event ID
| 1571 | HistoryEventList_yM61 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1572 | HistoryEventList_dH61 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1573 | HistoryEventList_ms61 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1574 | HistoryEventList_ID62 | U16 |  |  |  |  | R | The 62th most recent historical event ID
| 1575 | HistoryEventList_yM62 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1576 | HistoryEventList_dH62 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1577 | HistoryEventList_ms62 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1578 | HistoryEventList_ID63 | U16 |  |  |  |  | R | The 63th most recent historical event ID
| 1579 | HistoryEventList_yM63 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 157A | HistoryEventList_dH63 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 157B | HistoryEventList_ms63 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 157C | HistoryEventList_ID64 | U16 |  |  |  |  | R | The 64th most recent historical event ID
| 157D | HistoryEventList_yM64 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 157E | HistoryEventList_dH64 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 157F | HistoryEventList_ms64 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1580 | HistoryEventList_ID65 | U16 |  |  |  |  | R | The 65th most recent historical event ID
| 1581 | HistoryEventList_yM65 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1582 | HistoryEventList_dH65 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1583 | HistoryEventList_ms65 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1584 | HistoryEventList_ID66 | U16 |  |  |  |  | R | The 66th most recent historical event ID
| 1585 | HistoryEventList_yM66 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1586 | HistoryEventList_dH66 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1587 | HistoryEventList_ms66 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1588 | HistoryEventList_ID67 | U16 |  |  |  |  | R | The 67th most recent historical event ID
| 1589 | HistoryEventList_yM67 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 158A | HistoryEventList_dH67 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 158B | HistoryEventList_ms67 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 158C | HistoryEventList_ID68 | U16 |  |  |  |  | R | The 68th most recent historical event ID
| 158D | HistoryEventList_yM68 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 158E | HistoryEventList_dH68 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 158F | HistoryEventList_ms68 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1590 | HistoryEventList_ID69 | U16 |  |  |  |  | R | The 69th most recent historical event ID
| 1591 | HistoryEventList_yM69 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1592 | HistoryEventList_dH69 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1593 | HistoryEventList_ms69 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1594 | HistoryEventList_ID70 | U16 |  |  |  |  | R | The 70th most recent historical event ID
| 1595 | HistoryEventList_yM70 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1596 | HistoryEventList_dH70 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1597 | HistoryEventList_ms70 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1598 | HistoryEventList_ID71 | U16 |  |  |  |  | R | The 71th most recent historical event ID
| 1599 | HistoryEventList_yM71 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 159A | HistoryEventList_dH71 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 159B | HistoryEventList_ms71 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 159C | HistoryEventList_ID72 | U16 |  |  |  |  | R | The 72th most recent historical event ID
| 159D | HistoryEventList_yM72 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 159E | HistoryEventList_dH72 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 159F | HistoryEventList_ms72 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15A0 | HistoryEventList_ID73 | U16 |  |  |  |  | R | The 73th most recent historical event ID
| 15A1 | HistoryEventList_yM73 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15A2 | HistoryEventList_dH73 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15A3 | HistoryEventList_ms73 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15A4 | HistoryEventList_ID74 | U16 |  |  |  |  | R | The 74th most recent historical event ID
| 15A5 | HistoryEventList_yM74 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15A6 | HistoryEventList_dH74 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15A7 | HistoryEventList_ms74 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15A8 | HistoryEventList_ID75 | U16 |  |  |  |  | R | The 75th most recent historical event ID
| 15A9 | HistoryEventList_yM75 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15AA | HistoryEventList_dH75 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15AB | HistoryEventList_ms75 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15AC | HistoryEventList_ID76 | U16 |  |  |  |  | R | The 76th most recent historical event ID
| 15AD | HistoryEventList_yM76 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15AE | HistoryEventList_dH76 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15AF | HistoryEventList_ms76 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15B0 | HistoryEventList_ID77 | U16 |  |  |  |  | R | The 77th most recent historical event ID
| 15B1 | HistoryEventList_yM77 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15B2 | HistoryEventList_dH77 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15B3 | HistoryEventList_ms77 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15B4 | HistoryEventList_ID78 | U16 |  |  |  |  | R | The 78th most recent historical event ID
| 15B5 | HistoryEventList_yM78 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15B6 | HistoryEventList_dH78 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15B7 | HistoryEventList_ms78 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15B8 | HistoryEventList_ID79 | U16 |  |  |  |  | R | The 79th most recent historical event ID
| 15B9 | HistoryEventList_yM79 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15BA | HistoryEventList_dH79 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15BB | HistoryEventList_ms79 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15BC | HistoryEventList_ID80 | U16 |  |  |  |  | R | The 80th most recent historical event ID
| 15BD | HistoryEventList_yM80 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15BE | HistoryEventList_dH80 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15BF | HistoryEventList_ms80 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15C0 | HistoryEventList_ID81 | U16 |  |  |  |  | R | The 81th most recent historical event ID
| 15C1 | HistoryEventList_yM81 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15C2 | HistoryEventList_dH81 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15C3 | HistoryEventList_ms81 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15C4 | HistoryEventList_ID82 | U16 |  |  |  |  | R | The 82th most recent historical event ID
| 15C5 | HistoryEventList_yM82 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15C6 | HistoryEventList_dH82 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15C7 | HistoryEventList_ms82 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15C8 | HistoryEventList_ID83 | U16 |  |  |  |  | R | The 83th most recent historical event ID
| 15C9 | HistoryEventList_yM83 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15CA | HistoryEventList_dH83 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15CB | HistoryEventList_ms83 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15CC | HistoryEventList_ID84 | U16 |  |  |  |  | R | The 84th most recent historical event ID
| 15CD | HistoryEventList_yM84 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15CE | HistoryEventList_dH84 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15CF | HistoryEventList_ms84 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15D0 | HistoryEventList_ID85 | U16 |  |  |  |  | R | The 85th most recent historical event ID
| 15D1 | HistoryEventList_yM85 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15D2 | HistoryEventList_dH85 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15D3 | HistoryEventList_ms85 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15D4 | HistoryEventList_ID86 | U16 |  |  |  |  | R | The 86th most recent historical event ID
| 15D5 | HistoryEventList_yM86 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15D6 | HistoryEventList_dH86 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15D7 | HistoryEventList_ms86 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15D8 | HistoryEventList_ID87 | U16 |  |  |  |  | R | The 87th most recent historical event ID
| 15D9 | HistoryEventList_yM87 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15DA | HistoryEventList_dH87 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15DB | HistoryEventList_ms87 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15DC | HistoryEventList_ID88 | U16 |  |  |  |  | R | The 88th most recent historical event ID
| 15DD | HistoryEventList_yM88 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15DE | HistoryEventList_dH88 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15DF | HistoryEventList_ms88 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15E0 | HistoryEventList_ID89 | U16 |  |  |  |  | R | The 89th most recent historical event ID
| 15E1 | HistoryEventList_yM89 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15E2 | HistoryEventList_dH89 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15E3 | HistoryEventList_ms89 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15E4 | HistoryEventList_ID90 | U16 |  |  |  |  | R | The 90th most recent historical event ID
| 15E5 | HistoryEventList_yM90 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15E6 | HistoryEventList_dH90 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15E7 | HistoryEventList_ms90 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15E8 | HistoryEventList_ID91 | U16 |  |  |  |  | R | The 91th most recent historical event ID
| 15E9 | HistoryEventList_yM91 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15EA | HistoryEventList_dH91 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15EB | HistoryEventList_ms91 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15EC | HistoryEventList_ID92 | U16 |  |  |  |  | R | The 92th most recent historical event ID
| 15ED | HistoryEventList_yM92 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15EE | HistoryEventList_dH92 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15EF | HistoryEventList_ms92 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15F0 | HistoryEventList_ID93 | U16 |  |  |  |  | R | The 93th most recent historical event ID
| 15F1 | HistoryEventList_yM93 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15F2 | HistoryEventList_dH93 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15F3 | HistoryEventList_ms93 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15F4 | HistoryEventList_ID94 | U16 |  |  |  |  | R | The 94th most recent historical event ID
| 15F5 | HistoryEventList_yM94 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15F6 | HistoryEventList_dH94 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15F7 | HistoryEventList_ms94 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15F8 | HistoryEventList_ID95 | U16 |  |  |  |  | R | The 95th most recent historical event ID
| 15F9 | HistoryEventList_yM95 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15FA | HistoryEventList_dH95 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15FB | HistoryEventList_ms95 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 15FC | HistoryEventList_ID96 | U16 |  |  |  |  | R | The 96th most recent historical event ID
| 15FD | HistoryEventList_yM96 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 15FE | HistoryEventList_dH96 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 15FF | HistoryEventList_ms96 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1600 | HistoryEventList_ID97 | U16 |  |  |  |  | R | The 97th most recent historical event ID
| 1601 | HistoryEventList_yM97 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1602 | HistoryEventList_dH97 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1603 | HistoryEventList_ms97 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1604 | HistoryEventList_ID98 | U16 |  |  |  |  | R | The 98th most recent historical event ID
| 1605 | HistoryEventList_yM98 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 1606 | HistoryEventList_dH98 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 1607 | HistoryEventList_ms98 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1608 | HistoryEventList_ID99 | U16 |  |  |  |  | R | The 99th most recent historical event ID
| 1609 | HistoryEventList_yM99 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 160A | HistoryEventList_dH99 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 160B | HistoryEventList_ms99 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 160C | HistoryEventList_ID100 | U16 |  |  |  |  | R | The 100th most recent historical event ID
| 160D | HistoryEventList_yM100 | U16 |  |  |  |  | R | High byte: the lower two digits of the year's decimal number; Low byte: month.
| 160E | HistoryEventList_dH100 | U16 |  |  |  |  | R | High byte: date; Low byte: hour.
| 160F | HistoryEventList_ms100 | U16 |  |  |  |  | R | High byte: minutes; Low byte: seconds.
| 1610 | EnergyStatistics1 | U32 | 0.01 | kWh |  |  | R | Article 1 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1611
| 1612 | EnergyStatistics2 | U32 | 0.01 | kWh |  |  | R | Article 2 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1613
| 1614 | EnergyStatistics3 | U32 | 0.01 | kWh |  |  | R | Article 3 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1615
| 1616 | EnergyStatistics4 | U32 | 0.01 | kWh |  |  | R | Article 4 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1617
| 1618 | EnergyStatistics5 | U32 | 0.01 | kWh |  |  | R | Article 5 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1619
| 161A | EnergyStatistics6 | U32 | 0.01 | kWh |  |  | R | Article 6 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
161B
| 161C | EnergyStatistics7 | U32 | 0.01 | kWh |  |  | R | Article 7 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
161D
| 161E | EnergyStatistics8 | U32 | 0.01 | kWh |  |  | R | Article 8 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
161F
| 1620 | EnergyStatistics9 | U32 | 0.01 | kWh |  |  | R | Article 9 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1621
| 1622 | EnergyStatistics10 | U32 | 0.01 | kWh |  |  | R | Article 10 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1623
| 1624 | EnergyStatistics11 | U32 | 0.01 | kWh |  |  | R | Article 11 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1625
| 1626 | EnergyStatistics12 | U32 | 0.01 | kWh |  |  | R | Article 12 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1627
| 1628 | EnergyStatistics13 | U32 | 0.01 | kWh |  |  | R | Article 13 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1629
| 162A | EnergyStatistics14 | U32 | 0.01 | kWh |  |  | R | Article 14 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
162B
| 162C | EnergyStatistics15 | U32 | 0.01 | kWh |  |  | R | Article 15 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
162D
| 162E | EnergyStatistics16 | U32 | 0.01 | kWh |  |  | R | Article 16 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
162F
| 1630 | EnergyStatistics17 | U32 | 0.01 | kWh |  |  | R | Article 17 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1631
| 1632 | EnergyStatistics18 | U32 | 0.01 | kWh |  |  | R | Article 18 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1633
| 1634 | EnergyStatistics19 | U32 | 0.01 | kWh |  |  | R | Article 19 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1635
| 1636 | EnergyStatistics20 | U32 | 0.01 | kWh |  |  | R | Article 20 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1637
| 1638 | EnergyStatistics21 | U32 | 0.01 | kWh |  |  | R | Article 21 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1639
| 163A | EnergyStatistics22 | U32 | 0.01 | kWh |  |  | R | Article 22 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
163B
| 163C | EnergyStatistics23 | U32 | 0.01 | kWh |  |  | R | Article 23 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
163D
| 163E | EnergyStatistics24 | U32 | 0.01 | kWh |  |  | R | Article 24 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
163F
| 1640 | EnergyStatistics25 | U32 | 0.01 | kWh |  |  | R | Article 25 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1641
| 1642 | EnergyStatistics26 | U32 | 0.01 | kWh |  |  | R | Article 26 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1643
| 1644 | EnergyStatistics27 | U32 | 0.01 | kWh |  |  | R | Article 27 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1645
| 1646 | EnergyStatistics28 | U32 | 0.01 | kWh |  |  | R | Article 28 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1647
| 1648 | EnergyStatistics29 | U32 | 0.01 | kWh |  |  | R | Article 29 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1649
| 164A | EnergyStatistics30 | U32 | 0.01 | kWh |  |  | R | Article 30 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
164B
| 164C | EnergyStatistics31 | U32 | 0.01 | kWh |  |  | R | Article 31 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
164D
| 164E | EnergyStatistics32 | U32 | 0.01 | kWh |  |  | R | Article 32 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
164F
| 1650 | EnergyStatistics33 | U32 | 0.01 | kWh |  |  | R | Article 33 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1651
| 1652 | EnergyStatistics34 | U32 | 0.01 | kWh |  |  | R | Article 34 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1653
| 1654 | EnergyStatistics35 | U32 | 0.01 | kWh |  |  | R | Article 35 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1655
| 1656 | EnergyStatistics36 | U32 | 0.01 | kWh |  |  | R | Article 36 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1657
| 1658 | EnergyStatistics37 | U32 | 0.01 | kWh |  |  | R | Article 37 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
1659
| 165A | EnergyStatistics38 | U32 | 0.01 | kWh |  |  | R | Article 38 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
165B
| 165C | EnergyStatistics39 | U32 | 0.01 | kWh |  |  | R | Article 39 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
165D
| 165E | EnergyStatistics40 | U32 | 0.01 | kWh |  |  | R | Article 40 of historical electrical energy statistics. The corresponding date and time refer to the setting register of energy statistics return.
165F
| 2000 | AddressMask_Config_Core1 | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field is plus 1. 0 means invalid; 1 means valid. |  | E0000000 | 0000007F
2001
2002
2003
| 2004 | Country_Code | U16 |  |  |  |  | RW | Safety country, used for storage |  | 1 | 16
| 2005 | Safety_Version | U16 |  |  |  |  | RW | The version number of the safety parameters of the communication host (upper computer). |  | 1 | 32
| 2006 | Factory_Reset | U16 |  |  | 1 | 255 | RW | Restore factory registers; The bit value is 1 valid. Bit0: Clear battery Bit1: Clear event record Bit2: Restore default values ​​for all function configuration parameters When reading, return the status of the last write operation: 0x0000: success 0x0001-0x00FF: operating 0xFFFB: The operation failed and the controller refused to respond (maybe the controller is busy or the configuration is wrong) 0xFFFC: The operation failed and the controller did not respond 0xFFFD: Operation failed, current function is forbidden 0xFFFE: Operation failed, parameter access failed 0xFFFF: The operation failed, the input parameter is wrong |  | 1 | 64
| 2007 | Safety_Name1 | ASCII |  |  |  |  | RW | The first and second place in the name of the safety-regulated country. The upper 8 bits of the register store the first digit of the safety name; The lower 8 bits of the register store the second bit of the safety name. |  |  | 0
| 2008 | Safety_Name2 | ASCII |  |  |  |  | RW | The third and fourth place in the name of the safety-regulated country. The upper 8 bits of the register store the third digit of the safety name; The lower 8 bits of the register store the 4th bit of the safety name. |  |  | 0
| 2009 | Safety_Name3 | ASCII |  |  |  |  | RW | The 5th and 6th place in the name of the safety-regulated country. The upper 8 bits of the register store the 5th digit of the safety name; The lower 8 bits of the register store the 6th bit of the safety name. |  |  | 0
| 200A | Safety_Name4 | ASCII |  |  |  |  | RW | The 7th and 8th place in the name of the safety-regulated country. The upper 8 bits of the register store the 7th bit of the safety name; The lower 8 bits of the register store the 8th bit of the safety name. |  |  | 0
| 200B | Safety_Name5 | ASCII |  |  |  |  | RW | The ninth and tenth place in the name of safety regulations. The upper 8 bits of the register store the 9th bit of the safety name; The lower 8 bits of the register store the 10th bit of the safety name. |  |  | 0
| 200C | [10 empty] | 0
| 200D | [10 empty] | 0
| 200E | [10 empty] | 0
| 200F | [10 empty] | 0
| 2010 | [10 empty] | 0
| 2011 | [10 empty] | 0
| 2012 | [10 empty] | 0
| 2013 | [10 empty] | 0
| 2014 | [10 empty] | 0
| 2015 | [10 empty] | 0
| 2016 | [10 empty] | 0
| 2017 | [10 empty] | 0
| 2018 | [10 empty] | 0
| 2019 | [10 empty] | 0
| 201A | [10 empty] | 0
| 201B | [10 empty] | 0
| 201C | [10 empty] | 0
| 201D | [10 empty] | 0
| 201E | [10 empty] | 0
| 201F | [10 empty] | 0
| 2020 | [10 empty] | 0
| 2021 | [10 empty] | 0
| 2022 | [10 empty] | 0
| 2023 | [10 empty] | 0
| 2024 | [10 empty] | 0
| 2025 | [10 empty] | 0
| 2026 | [10 empty] | 0
| 2027 | [10 empty] | 0
| 2028 | [10 empty] | 0
| 2029 | [10 empty] | 0
| 202A | [10 empty] | 0
| 202B | [10 empty] | 0
| 202C | [10 empty] | 0
| 202D | [10 empty] | 0
| 202E | [10 empty] | 0
| 202F | [10 empty] | 0
| 2030 | [10 empty] | 0
| 2031 | [10 empty] | 0
| 2032 | [10 empty] | 0
| 2033 | [10 empty] | 0
| 2034 | [10 empty] | 0
| 2035 | [10 empty] | 0
| 2036 | [10 empty] | 0
| 2037 | [10 empty] | 0
| 2038 | [10 empty] | 0
| 2039 | [10 empty] | 0
| 203A | [10 empty] | 0
| 203B | [10 empty] | 0
| 203C | [10 empty] | 0
| 203D | Remote_Upgrade_Control | U16 |  |  |  |  | W | Remote upgrade control register. High byte. Writing 0xA5 is valid. The low byte contains the chip combination that needs to be upgraded, and the explanation of each bit is as follows: Bit0: communication board; Bit1: control board 1 (main DSP); Bit2: control board 2 (secondary DSP); Bit3: Fuse |  | 1 | 2.3058e+18
| 203E | Local_Upgrade_Control | U16 |  |  |  |  | W | High byte. Writing 0xA5 is valid. The low byte contains the chip combination that needs to be upgraded, and the explanation of each bit is as follows: Bit0: communication board; Bit1: control board 1 (main DSP); Bit2: control board 2 (secondary DSP); Bit3: Fuse |  | 1 | 4.6117e+18
| 203F | Local_Upgrade_Status | U16 |  |  |  |  | R | Current upgrade progress The high byte indicates the current target chip to be upgraded: 0x00: Not in the upgrade state; 0x01: Main DSP upgrade; 0x02: Secondary DSP upgrade; 0x03: ARM upgrade; 0x04: FUSE upgrade; The low byte indicates the current upgrade progress: The progress range is 0-100% |  | 1 | 9.2234e+18
BMS（0x9000-0x9FFF）
| 9000 | AddressMask_BMS1_System | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid. |  | 00000001 | 00FFFFFF
9001
9002
9003
| 9004 | BMS_Sys_Time | U32 |  |  |  |  | R | BMS system clock Bit0-5: second, range 0-59 Bit6-11: minute, range 0-59 Bit12-16: hour, range 0-23 Bit17-21: day, range 1-31 Bit22-25: month, range 1-12 Bit26-31: year, range 0-63 (starting in 2000) |  | 1 | 16
| 9005 | [9 empty] | 1 | 32
| 9006 | BMS_CAN_Version | U16 |  |  |  |  | R | CAN protocol version number |  | 1 | 64
| 9007 | BMS_Manufacture_Name0 | U16 |  |  |  |  | R | Manufacturer Information 0 |  | 1 | 128
| 9008 | BMS_Manufacture_Name1 | U16 |  |  |  |  | R | Manufacturer Information 1 |  | 1 | 256
| 9009 | BMS_Manufacture_Name2 | U16 |  |  |  |  | R | Manufacturer Information 2 |  | 1 | 512
| 900A | BMS_Manufacture_Name3 | U16 |  |  |  |  | R | Manufacturer Information 3 |  | 1 | 1024
| 900B | BMS_Version | U16 |  |  |  |  | R | BMS version number |  | 1 | 2048
| 900C | Cell_Type | U16 |  |  |  |  | R | Cell type |  | 1 | 4096
| 900D | BaPack_Number | U16 |  |  |  |  | R | High 8 bits: the number of battery packs in parallel Lower 8 bits: the number of battery strings in the battery pack |  | 1 | 8192
| 900E | Realtime_Capacity | U16 | 1 | % |  |  | R | Real-time remaining capacity |  | 1 | 16384
| 900F | Total_Voltage | U16 | 0.1 | V |  |  | R | Total voltage |  | 1 | 32768
| 9010 | Total_Current | U16 | 0.1 | A |  |  | R | Total current |  | 1 | 65536
| 9011 | Cell_Average_Temperature | U16 | 0.1 | °C |  |  | R | Average cell temperature |  | 1 | 131072
| 9012 | SOC | U16 | 1 | % |  |  | R | State of charge |  | 1 | 262144
| 9013 | SOH | U16 | 1 | % |  |  | R | Health |  | 1 | 524288
| 9014 | BMS_Sys_Protect0 | U16 |  |  |  |  | R | BMS system protection information0 |  | 1 | 1048576
| 9015 | BMS_Sys_Protect1 | U16 |  |  |  |  | R | BMS system protection information 1 |  | 1 | 2097152
| 9016 | BMS_Sys_Alarm0 | U16 |  |  |  |  | R | BMS system alarm information 0 |  | 1 | 4194304
| 9017 | BMS_Sys_Alarm1 | U16 |  |  |  |  | R | BMS system alarm information 1 |  | 1 | 8388608
| 9018 | [10 empty] | 0
| 9019 | [10 empty] | 0
| 901A | [10 empty] | 0
| 901B | [10 empty] | 0
| 901C | [10 empty] | 0
| 901D | [10 empty] | 0
| 901E | [10 empty] | 0
| 901F | [10 empty] | 0
| 9020 | BMS_Inquire | U16 |  |  |  |  | RW | Battery query control word Bit0-7: The serial number of the battery pack to be queried, the valid range is 0~15, and 0 means the first battery pack Bit8-11: The serial number of the battery pack to be queried, the valid range is 0~15, and 0 means the first battery pack Bit12-15: The serial number of the fault to be queried, the valid range is 0~5, and 0 means the most recent fault |  | 1 | 4294967296
| 9021 | [10 empty] | 0
| 9022 | [10 empty] | 0
| 9023 | [10 empty] | 0
| 9024 | [10 empty] | 0
| 9025 | [10 empty] | 0
| 9026 | [10 empty] | 0
| 9027 | [10 empty] | 0
| 9028 | [10 empty] | 0
| 9029 | [10 empty] | 0
| 902A | [10 empty] | 0
| 902B | [10 empty] | 0
| 902C | [10 empty] | 0
| 902D | [10 empty] | 0
| 902E | [10 empty] | 0
| 902F | [10 empty] | 0
| 9030 | [10 empty] | 0
| 9031 | [10 empty] | 0
| 9032 | [10 empty] | 0
| 9033 | [10 empty] | 0
| 9034 | [10 empty] | 0
| 9035 | [10 empty] | 0
| 9036 | [10 empty] | 0
| 9037 | [10 empty] | 0
| 9038 | [10 empty] | 0
| 9039 | [10 empty] | 0
| 903A | [10 empty] | 0
| 903B | [10 empty] | 0
| 903C | [10 empty] | 0
| 903D | [10 empty] | 0
| 903E | [10 empty] | 0
| 903F | [10 empty] | 0
| 9040 | AddressMask_BMS2_Realtime | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid. |  | 01FFFFFF | FFFFFFFF
9041
9042
9043
| 9044 | Pack_RT_ID | U16 |  |  |  |  | R | Real-time data battery pack number. High 8 bits: battery pack serial number Lower 8 bits: battery pack serial number" |  | 1 | 16
| 9045 | Pack_RT_Timestamp | U32 |  |  |  |  | R | Real-time data timestamp |  | 1 | 32
| 9046 | [9 empty] | 1 | 64
| 9047 | Pack_RT_SN0 | U16 |  |  |  |  | R | Device serial number 0 |  | 1 | 128
| 9048 | Pack_RT_SN1 | U16 |  |  |  |  | R | Device serial number 1 |  | 1 | 256
| 9049 | Pack_RT_SN2 | U16 |  |  |  |  | R | Device serial number 2 |  | 1 | 512
| 904A | Pack_RT_SN3 | U16 |  |  |  |  | R | Device serial number 3 |  | 1 | 1024
| 904B | Pack_RT_SN4 | U16 |  |  |  |  | R | Device serial number 4 |  | 1 | 2048
| 904C | Pack_RT_SN5 | U16 |  |  |  |  | R | Device serial number 5 |  | 1 | 4096
| 904D | Pack_RT_SN6 | U16 |  |  |  |  | R | Device serial number 6 |  | 1 | 8192
| 904E | Pack_RT_SN7 | U16 |  |  |  |  | R | Device serial number 7 |  | 1 | 16384
| 904F | Pack_RT_SN8 | U16 |  |  |  |  | R | Device serial number 8 |  | 1 | 32768
| 9050 | Pack_RT_SN9 | U16 |  |  |  |  | R | Device serial number 9 |  | 1 | 65536
| 9051 | Pack_RT_Cell_Voltage1 | U16 | 0.001 | V |  |  | R | Cell 1 voltage |  | 1 | 131072
| 9052 | Pack_RT_Cell_Voltage2 | U16 | 0.001 | V |  |  | R | Cell 2 voltage |  | 1 | 262144
| 9053 | Pack_RT_Cell_Voltage3 | U16 | 0.001 | V |  |  | R | Cell 3 voltage |  | 1 | 524288
| 9054 | Pack_RT_Cell_Voltage4 | U16 | 0.001 | V |  |  | R | Cell 4 voltage |  | 1 | 1048576
| 9055 | Pack_RT_Cell_Voltage5 | U16 | 0.001 | V |  |  | R | Cell 5 voltage |  | 1 | 2097152
| 9056 | Pack_RT_Cell_Voltage6 | U16 | 0.001 | V |  |  | R | Cell 6 voltage |  | 1 | 4194304
| 9057 | Pack_RT_Cell_Voltage7 | U16 | 0.001 | V |  |  | R | Cell 7 voltage |  | 1 | 8388608
| 9058 | Pack_RT_Cell_Voltage8 | U16 | 0.001 | V |  |  | R | Cell 8 voltage |  | 1 | 16777216
| 9059 | Pack_RT_Cell_Voltage9 | U16 | 0.001 | V |  |  | R | Cell 9 voltage |  | 1 | 33554432
| 905A | Pack_RT_Cell_Voltage10 | U16 | 0.001 | V |  |  | R | Cell 10 voltage |  | 1 | 67108864
| 905B | Pack_RT_Cell_Voltage11 | U16 | 0.001 | V |  |  | R | Cell 11 voltage |  | 1 | 134217728
| 905C | Pack_RT_Cell_Voltage12 | U16 | 0.001 | V |  |  | R | Cell 12 voltage |  | 1 | 268435456
| 905D | Pack_RT_Cell_Voltage13 | U16 | 0.001 | V |  |  | R | Cell 13 voltage |  | 1 | 536870912
| 905E | Pack_RT_Cell_Voltage14 | U16 | 0.001 | V |  |  | R | Cell 14 voltage |  | 1 | 1073741824
| 905F | Pack_RT_Cell_Voltage15 | U16 | 0.001 | V |  |  | R | Cell 15 voltage |  | 1 | 2147483648
| 9060 | Pack_RT_Cell_Voltage16 | U16 | 0.001 | V |  |  | R | Cell 16 voltage |  | 1 | 4294967296
| 9061 | Pack_RT_Cell_Voltage17 | U16 | 0.001 | V |  |  | R | Cell 17 voltage |  | 1 | 8589934592
| 9062 | Pack_RT_Cell_Voltage18 | U16 | 0.001 | V |  |  | R | Cell 18 voltage |  | 1 | 17179869184
| 9063 | Pack_RT_Cell_Voltage19 | U16 | 0.001 | V |  |  | R | Cell 19 voltage |  | 1 | 34359738368
| 9064 | Pack_RT_Cell_Voltage20 | U16 | 0.001 | V |  |  | R | Cell 20 voltage |  | 1 | 68719476736
| 9065 | Pack_RT_Cell_Voltage21 | U16 | 0.001 | V |  |  | R | Cell 21 voltage |  | 1 | 137438953472
| 9066 | Pack_RT_Cell_Voltage22 | U16 | 0.001 | V |  |  | R | Battery 22 voltage |  | 1 | 274877906944
| 9067 | Pack_RT_Cell_Voltage23 | U16 | 0.001 | V |  |  | R | Battery 23 voltage |  | 1 | 549755813888
| 9068 | Pack_RT_Cell_Voltage24 | U16 | 0.001 | V |  |  | R | Cell 24 voltage |  | 1 | 1099511627776
| 9069 | Pack_RT_Cell_Max_Voltage | U16 | 0.001 | V |  |  | R | The highest voltage of the battery |  | 1 | 2199023255552
| 906A | Pack_RT_Cell_Min_Voltage | U16 | 0.001 | V |  |  | R | Minimum battery voltage |  | 1 | 4398046511104
| 906B | Pack_RT_Temperature1_Pack | I16 | 0.1 | °C |  |  | R | Battery pack temperature 1 |  | 1 | 8796093022208
| 906C | Pack_RT_Temperature2_Pack | I16 | 0.1 | °C |  |  | R | Battery pack temperature 2 |  | 1 | 17592186044416
| 906D | Pack_RT_Temperature3_Pack | I16 | 0.1 | °C |  |  | R | Battery pack temperature 3 |  | 1 | 35184372088832
| 906E | Pack_RT_Temperature4_Pack | I16 | 0.1 | °C |  |  | R | Battery pack temperature 4 |  | 1 | 70368744177664
| 906F | Pack_RT_Temperature_MOS | I16 | 0.1 | °C |  |  | R | MOS tube temperature |  | 1 | 140737488355328
| 9070 | Pack_RT_Temperature_Env | I16 | 0.1 | °C |  |  | R | Ambient temperature in the battery pack |  | 1 | 281474976710656
| 9071 | Pack_RT_Current | I16 | 0.1 | A |  |  | R | Battery pack current |  | 1 | 562949953421312
| 9072 | Pack_RT_Remaining_Capacity | U16 | 0.1 | Ah |  |  | R | The remaining capacity |  | 1 | 1125900000000000
| 9073 | Pack_RT_FullCharge_Capacity | U16 | 0.1 | Ah |  |  | R | Full charge capacity |  | 1 | 2251800000000000
| 9074 | Pack_RT_Cycles | U16 | 1 | times |  |  | R | Cycles |  | 1 | 4503600000000000
| 9075 | Pack_RT_Balance_State | U16 |  |  |  |  | R | Equilibrium |  | 1 | 9007200000000000
| 9076 | Pack_RT_Alarm_State | U16 |  |  |  |  | R | Alarm status |  | 1 | 18014400000000000
| 9077 | Pack_RT_Protect_State | U16 |  |  |  |  | R | Protection status |  | 1 | 36028800000000000
| 9078 | Pack_RT_Fault_State | U16 |  |  |  |  | R | Fault state |  | 1 | 72057600000000000
| 9079 | Pack_RT_Total_Voltage | U16 | 0.01 | V |  |  | R | Total Voltage
| 907A | Pack_RT_SOC | U16 | 1 | % |  |  | R | SOC
| 907B | [10 empty] | 0
| 907C | [10 empty] | 0
| 907D | [10 empty] | 0
| 907E | [10 empty] | 0
| 907F | [10 empty] | 0
| 9080 | AddressMask_BMS3_Fault | U64 |  |  |  |  | R | Each bit of this field corresponds to the validity of 64 addresses above the address of this field (including the address of this field). Bit4 represents the address where the highest bit address of this field plus 1 is located. 0 means invalid; 1 means valid |  | 00FFFFFF | FFFFFFFF
9081
9082
9083
| 9084 | Pack_Fault_ID | U16 |  |  |  |  | R | Real-time faulty battery pack number. Bit0-7: The serial number of the battery pack to be queried, the valid range is 0~15, and 0 means the first battery pack Bit8-11: The serial number of the battery pack to be queried, the valid range is 0~15, and 0 means the first battery pack Bit12-15: The serial number of the queried fault, the valid range is 0~5, 0 means the most recent fault |  | 1 | 16
| 9085 | Pack_Fault_Timestamp | U32 |  |  |  |  | R | Fault data timestamp |  | 1 | 32
| 9086 | [9 empty] | 1 | 64
| 9087 | Pack_Fault_SN0 | U16 |  |  |  |  | R | Device serial number 0 |  | 1 | 128
| 9088 | Pack_Fault_SN1 | U16 |  |  |  |  | R | Device serial number 1 |  | 1 | 256
| 9089 | Pack_Fault_SN2 | U16 |  |  |  |  | R | Device serial number 2 |  | 1 | 512
| 908A | Pack_Fault_SN3 | U16 |  |  |  |  | R | Device serial number 3 |  | 1 | 1024
| 908B | Pack_Fault_SN4 | U16 |  |  |  |  | R | Device serial number 4 |  | 1 | 2048
| 908C | Pack_Fault_SN5 | U16 |  |  |  |  | R | Device serial number 5 |  | 1 | 4096
| 908D | Pack_Fault_SN6 | U16 |  |  |  |  | R | Device serial number 6 |  | 1 | 8192
| 908E | Pack_Fault_SN7 | U16 |  |  |  |  | R | Device serial number 7 |  | 1 | 16384
| 908F | Pack_Fault_SN8 | U16 |  |  |  |  | R | Device serial number 8 |  | 1 | 32768
| 9090 | Pack_Fault_SN9 | U16 |  |  |  |  | R | Device serial number 9 |  | 1 | 65536
| 9091 | Pack_Fault_Cell_Voltage1 | U16 | 0.001 | V |  |  | R | Cell 1 voltage |  | 1 | 131072
| 9092 | Pack_Fault_Cell_Voltage2 | U16 | 0.001 | V |  |  | R | Cell 2 voltage |  | 1 | 262144
| 9093 | Pack_Fault_Cell_Voltage3 | U16 | 0.001 | V |  |  | R | Cell 3 voltage |  | 1 | 524288
| 9094 | Pack_Fault_Cell_Voltage4 | U16 | 0.001 | V |  |  | R | Cell 4 voltage |  | 1 | 1048576
| 9095 | Pack_Fault_Cell_Voltage5 | U16 | 0.001 | V |  |  | R | Cell 5 voltage |  | 1 | 2097152
| 9096 | Pack_Fault_Cell_Voltage6 | U16 | 0.001 | V |  |  | R | Cell 6 voltage |  | 1 | 4194304
| 9097 | Pack_Fault_Cell_Voltage7 | U16 | 0.001 | V |  |  | R | Cell 7 voltage |  | 1 | 8388608
| 9098 | Pack_Fault_Cell_Voltage8 | U16 | 0.001 | V |  |  | R | Cell 8 voltage |  | 1 | 16777216
| 9099 | Pack_Fault_Cell_Voltage9 | U16 | 0.001 | V |  |  | R | Cell 9 voltage |  | 1 | 33554432
| 909A | Pack_Fault_Cell_Voltage10 | U16 | 0.001 | V |  |  | R | Cell 10 voltage |  | 1 | 67108864
| 909B | Pack_Fault_Cell_Voltage11 | U16 | 0.001 | V |  |  | R | Cell 11 voltage |  | 1 | 134217728
| 909C | Pack_Fault_Cell_Voltage12 | U16 | 0.001 | V |  |  | R | Cell 12 voltage |  | 1 | 268435456
| 909D | Pack_Fault_Cell_Voltage13 | U16 | 0.001 | V |  |  | R | Cell 13 voltage |  | 1 | 536870912
| 909E | Pack_Fault_Cell_Voltage14 | U16 | 0.001 | V |  |  | R | Cell 14 voltage |  | 1 | 1073741824
| 909F | Pack_Fault_Cell_Voltage15 | U16 | 0.001 | V |  |  | R | Cell 15 voltage |  | 1 | 2147483648
| 90A0 | Pack_Fault_Cell_Voltage16 | U16 | 0.001 | V |  |  | R | Cell 16 voltage |  | 1 | 4294967296
| 90A1 | Pack_Fault_Cell_Voltage17 | U16 | 0.001 | V |  |  | R | Cell 17 voltage |  | 1 | 8589934592
| 90A2 | Pack_Fault_Cell_Voltage18 | U16 | 0.001 | V |  |  | R | Cell 18 voltage |  | 1 | 17179869184
| 90A3 | Pack_Fault_Cell_Voltage19 | U16 | 0.001 | V |  |  | R | Cell 19 voltage |  | 1 | 34359738368
| 90A4 | Pack_Fault_Cell_Voltage20 | U16 | 0.001 | V |  |  | R | Cell 20 voltage |  | 1 | 68719476736
| 90A5 | Pack_Fault_Cell_Voltage21 | U16 | 0.001 | V |  |  | R | Cell 21 voltage |  | 1 | 137438953472
| 90A6 | Pack_Fault_Cell_Voltage22 | U16 | 0.001 | V |  |  | R | Battery 22 voltage |  | 1 | 274877906944
| 90A7 | Pack_Fault_Cell_Voltage23 | U16 | 0.001 | V |  |  | R | Battery 23 voltage |  | 1 | 549755813888
| 90A8 | Pack_Fault_Cell_Voltage24 | U16 | 0.001 | V |  |  | R | Cell 24 voltage |  | 1 | 1099511627776
| 90A9 | Pack_Fault_Cell_Max_Voltage | U16 | 0.001 | V |  |  | R | The highest voltage of the battery |  | 1 | 2199023255552
| 90AA | Pack_Fault_Cell_Min_Voltage | U16 | 0.001 | V |  |  | R | Minimum battery voltage |  | 1 | 4398046511104
| 90AB | Pack_Fault_Temperature1_Pack | I16 | 0.1 | °C |  |  | R | Battery pack temperature 1 |  | 1 | 8796093022208
| 90AC | Pack_Fault_Temperature2_Pack | I16 | 0.1 | °C |  |  | R | Battery pack temperature 2 |  | 1 | 17592186044416
| 90AD | Pack_Fault_Temperature3_Pack | I16 | 0.1 | °C |  |  | R | Battery pack temperature 3 |  | 1 | 35184372088832
| 90AE | Pack_Fault_Temperature4_Pack | I16 | 0.1 | °C |  |  | R | Battery pack temperature 4 |  | 1 | 70368744177664
| 90AF | Pack_Fault_Temperature_MOS | I16 | 0.1 | °C |  |  | R | MOS tube temperature |  | 1 | 140737488355328
| 90B0 | Pack_Fault_Temperature_Env | I16 | 0.1 | °C |  |  | R | Ambient temperature in the battery pack |  | 1 | 281474976710656
| 90B1 | Pack_Fault_Current | I16 | 0.1 | A |  |  | R | Battery pack current |  | 1 | 562949953421312
| 90B2 | Pack_Fault_Remaining_Capacity | U16 | 0.1 | Ah |  |  | R | The remaining capacity |  | 1 | 1125900000000000
| 90B3 | Pack_Fault_FullCharge_Capacity | U16 | 0.1 | Ah |  |  | R | Full charge capacity |  | 1 | 2251800000000000
| 90B4 | Pack_Fault_Total_Voltage | U16 | 0.01 | V |  |  | R | Total voltage |  | 1 | 4503600000000000
| 90B5 | Pack_Alarm_State | U16 |  |  |  |  | R | Alarm status |  | 1 | 9007200000000000
| 90B6 | Pack_Protect_State | U16 |  |  |  |  | R | Protection status |  | 1 | 18014400000000000
| 90B7 | Pack_Fault_State | U16 |  |  |  |  | R | Fault state |  | 1 | 36028800000000000
| 90B8 | [10 empty] | 0
| 90B9 | [10 empty] | 0
| 90BA | [10 empty] | 0
| 90BB | [10 empty] | 0
| 90BC | [10 empty] | 0
| 90BD | [10 empty] | 0
| 90BE | [10 empty] | 0
| 90BF | [10 empty] | 0

## Fault Addresses
Table | Byte | Bit | Field | No. | Remark | 告警源 | Category
Fault1 | byte 0 | bit 0 | GridOVP | 001 | Grid over-voltage | DSPM | Electricity grid
|  | bit 1 | GridUVP | 002 | Grid undervoltage | DSPM
|  | bit 2 | GridOFP | 003 | Grid Overfrequency | DSPM
|  | bit 3 | GridUFP | 004 | Grid Underfrequency | DSPM
|  | bit 4 | GFCI | 005 | Leakage current fault | DSPM&S
|  | bit 5 | OVRT | 006 | High penetration error | DSPM
|  | bit 6 | LVRT | 007 | Low penetration error | DSPM
|  | bit 7 | IslandFault | 008 | Islanding error | DSPM
| byte 1 | bit 0 | GridOVPInstant1 | 009 | Grid voltage transient value overvoltage 1 | DSPM
|  | bit 1 | GridOVPInstant2 | 010 | Grid voltage transient value overvoltage 2 | DSPM
|  | bit 2 | VGridLineFault | 011 | Grid line voltage error | DSPM
|  | bit 3 | InvOVP | 012 | Inverter voltage overvoltage | DSPM
|  | bit 4 |  | 013
|  | bit 5 |  | 014
|  | bit 6 |  | 015
|  | bit 7 |  | 016
Fault2 | byte 0 | bit 0 | HwADFaultIGrid | 017 | Grid current sampling error | DSPM | Sampling error
|  | bit 1 | HwADFaultDCI(AC) | 018 | Grid current DC component sampling error (AC side) | DSPM
|  | bit 2 | HwADFaultVGrid(DC) | 019 | Grid voltage sampling error (DC side) | DSPS
|  | bit 3 | HwADFaultVGrid(AC) | 020 | Grid voltage sampling error (AC side) | DSPM
|  | bit 4 | GFCIDeviceFault(DC) | 021 | Leakage current sampling error (DC side) | DSPS
|  | bit 5 | GFCIDeviceFault(AC) | 022 | Leakage current sampling error (AC side) | DSPM
|  | bit 6 | HwADFaultDCV | 023 | Load voltage DC component sampling error | DSPM
|  | bit 7 | HwADFaultIdc | 024 | DC input current sampling error | DSPS
| byte 1 | bit 0 | HwADFaultDCI(DC) | 025 | DC component sampling error of grid current (DC side) | DSPS
|  | bit 1 | HwADFaultIdcBranch | 026 | DC input branch current sampling error | DSPS
|  | bit 2 |  | 027
|  | bit 3 |  | 028
|  | bit 4 | ConsistentFault_GFCI | 029 | Leakage current consistency error | DSPS
|  | bit 5 | ConsistentFault_Vgrid | 030 | Grid voltage consistency error | DSPS
|  | bit 6 | ConsistentFault_DCI | 031 | DCI consistency error | DSPS
|  | bit 7 |  | 032
Fault3 | byte 0 | bit 0 | SpiCommFault(DC) | 033 | SPI communication error (DC side)
|  | bit 1 | SpiCommFault(AC) | 034 | SPI communication error (AC side)
|  | bit 2 | SChip_Fault | 035 | Chip error (DC side)
|  | bit 3 | MChip_Fault | 036 | Chip error (AC side)
|  | bit 4 | HwAuxPowerFault | 037 | Auxiliary power error
|  | bit 5 | InverterSoftStartFail | 038 | Inverter soft start failure | DSPM
|  | bit 6 |  | 039
|  | bit 7 |  | 040
| byte 1 | bit 0 | RelayFail | 041 | Relay detection failure | DSPM | System
|  | bit 1 | IsoFault | 042 | Low insulation impedance | DSPS
|  | bit 2 | PEConnectFault | 043 | Grounding error | DSPS
|  | bit 3 | PvConfigError | 044 | Input mode setting error | DSPS
|  | bit 4 | CTDisconnect | 045 | CT error | DSPM&S
|  | bit 5 | ReversalConnection | 046 | Input reversal error | DSPS
|  | bit 6 | ParallelFault | 047 | Parallel error | DSPM
|  | bit 7 | SNTypeFault | 048 | Serial number error | DSPM&S
Fault4 | byte 0 | bit 0 | TempFault_Bat | 049 | Battery temperature protection | DSPM&S | Temperature
|  | bit 1 | TempFault_HeatSink1 | 050 | Heat sink 1 temperature protection | DSPM&S
|  | bit 2 | TempFault_HeatSink2 | 051 | Heater 2 temperature protection | DSPM&S
|  | bit 3 | TempFault_HeatSink3 | 052 | Heater 3 temperature protection | DSPM&S
|  | bit 4 | TempFault_HeatSink4 | 053 | Heatsink 4 temperature protection | DSPM&S
|  | bit 5 | TempFault_HeatSink5 | 054 | Heatsink 5 temperature protection | DSPM&S
|  | bit 6 | TempFault_HeatSink6 | 055 | Radiator 6 temperature protection | DSPM&S
|  | bit 7 |  | 056
| byte 1 | bit 0 | TempFault_Env1 | 057 | Ambient temperature 1 protection | DSPM&S
|  | bit 1 | TempFault_Env2 | 058 | Ambient temperature 2 protection | DSPM&S
|  | bit 2 | TempFault_Inv1 | 059 | Module 1 temperature protection | DSPM&S
|  | bit 3 | TempFault_Inv2 | 060 | Module 2 temperature protection | DSPM&S
|  | bit 4 | TempFault_Inv3 | 061 | Module 3 temperature protection | DSPM&S
|  | bit 5 |  | 062
|  | bit 6 |  | 063
|  | bit 7 |  | 064
Fault5 | byte 0 | bit 0 | VbusRmsUnbalance | 065 | Bus voltage RMS unbalance | DSPM | Overvoltage
|  | bit 1 | VbusInstantUnbalance | 066 | Bus voltage transient value unbalance | DSPM
|  | bit 2 | BusUVP | 067 | Undervoltage of busbar during grid connection | DSPM
|  | bit 3 | BusZVP | 068 | Bus bar low voltage | DSPM
|  | bit 4 | PVOVP | 069 | PV overvoltage | DSPS
|  | bit 5 | BatOVP | 070 | Battery over-voltage | DSPS
|  | bit 6 | LLCBusOVP | 071 | LLCBus overvoltage protection | DSPS
|  | bit 7 | SwBusRmsOVP | 072 | Inverter bus voltage RMS software overvoltage | DSPM
| byte 1 | bit 0 | SwBusInstantOVP | 073 | Inverter bus voltage transient value software overvoltage | DSPM
|  | bit 1 | FlyingCapOVP | 074 | Flying Cross Capacitor Overvoltage Protection | DSPM&S
|  | bit 2 |  | 075
|  | bit 3 |  | 076
|  | bit 4 |  | 077
|  | bit 5 |  | 078
|  | bit 6 |  | 079
|  | bit 7 |  | 080
Fault6 | byte 0 | bit 0 | SwBatOCP | 081 | Battery overcurrent software protection | DSPS | Current
|  | bit 1 | DciOCP | 082 | Dci overcurrent protection | DSPM
|  | bit 2 | SwOCPInstant | 083 | Output transient current protection | DSPM
|  | bit 3 | SwBuckBoostOCP | 084 | BuckBoost software overcurrent | DSPS
|  | bit 4 | SwAcRmsOCP | 085 | Output RMS current protection | DSPM
|  | bit 5 | SwPvOCPInstant | 086 | PV instantaneous current overcurrent software protection | DSPS
|  | bit 6 | IpvUnbalance | 087 | PV parallel uneven current | DSPS
|  | bit 7 | IacUnbalance | 088 | Output current unbalance | DSPM
| byte 1 | bit 0 | SwPvOCP | 089 | PV software overcurrent protection | DSPM&S
|  | bit 1 | IbalanceOCP | 090 | Balanced circuit overcurrent protection | DSPM&S
|  | bit 2 |  | 091
|  | bit 3 |  | 092
|  | bit 4 |  | 093
|  | bit 5 |  | 094
|  | bit 6 |  | 095
|  | bit 7 |  | 096
Fault7 | byte 0 | bit 0 | HwLLCBusOVP | 097 | LLC bus hardware overvoltage | DSPS | Hardware signals
|  | bit 1 | HwBusOVP | 098 | Inverter bus hardware overvoltage | DSPM
|  | bit 2 | HwBuckBoostOCP | 099 | BuckBoost hardware overcurrent | DSPS
|  | bit 3 | HwBatOCP | 100 | Battery hardware overcurrent | DSPS
|  | bit 4 |  | 101
|  | bit 5 | HwPVOCP | 102 | PV hardware overcurrent | DSPS
|  | bit 6 | HwACOCP | 103 | AC output hardware overcurrent | DSPM
|  | bit 7 |  | 104
| byte 1 | bit 0 | MeterCommFault | 105 | Power meter error | DSPM&S | Hardware signal reservation, overload
|  | bit 1 |  | 106
|  | bit 2 |  | 107
|  | bit 3 |  | 108
|  | bit 4 |  | 109
|  | bit 5 | Overload1 | 110 | Overload protection 1 | DSPM
|  | bit 6 | Overload2 | 111 | Overload protection 2 | DSPM
|  | bit 7 | Overload3 | 112 | Overload protection 3 | DSPM
Fault8 | byte 0 | bit 0 | OverTempDerating | 113 | Overtemperature derating | DSPM | Power derating | The fault word is only used to generate an alarm and does not directly put the system into a fault state.
|  | bit 1 | FreqDerating | 114 | Frequency down load | DSPM
|  | bit 2 | FreqLoading | 115 | Frequency loading | DSPM
|  | bit 3 | VoltDerating | 116 | Voltage down load | DSPM
|  | bit 4 | VoltLoading | 117 | Voltage loading | DSPM
|  | bit 5 |  | 118 |  | DSPM
|  | bit 6 |  | 119
|  | bit 7 |  | 120
| byte 1 | bit 0 |  | 121 |  |  | Shut down
|  | bit 1 |  | 122
|  | bit 2 |  | 123
|  | bit 3 | BatLowVoltageAlarm | 124 | Battery low voltage protection
|  | bit 4 | BatLowVoltageShut | 125 | Battery low voltage shutdown
|  | bit 5 |  | 126 | Battery low voltage pre-alarm
|  | bit 6 |  | 127
|  | bit 7 |  | 128
Fault9 | byte 0 | bit 0 | unrecoverHwAcOCP | 129 | Output hardware overcurrent permanent fault | DSPM | permenent
|  | bit 1 | unrecoverBusOVP | 130 | Bus overvoltage permanent fault | DSPM
|  | bit 2 | unrecoverHwBusOVP | 131 | Bus hardware over-voltage permanent fault | DSPM
|  | bit 3 | unrecoverIpvUnbalance | 132 | PV uneven flow permanent fault | DSPS
|  | bit 4 | unrecoverEPSBatOCP | 133 | Battery overcurrent permanent fault in EPS mode | DSPM
|  | bit 5 | unrecoverAcOCPInstant | 134 | Output transient overcurrent permanent fault | DSPM
|  | bit 6 | unrecoverIacUnbalance | 135 | Output current unbalance permanent fault | DSPM
|  | bit 7 |  | 136
| byte 1 | bit 0 | unrecoverPvConfigError | 137 | Input mode setting error permanent fault | DSPS
|  | bit 1 | unrecoverPVOCPInstant | 138 | Input overcurrent permanent fault | DSPS
|  | bit 2 | unrecoverHwPVOCP | 139 | Input hardware overcurrent permanent fault | DSPS
|  | bit 3 | unrecoverRelayFail | 140 | Relay permanent fault | DSPM
|  | bit 4 | unrecoverVbusUnbalance | 141 | Bus unbalance permanent fault | DSPM
|  | bit 5 | unrecoverSpdFail(DC) | 142 | Lightning protection permanent fault - DC side | DSPS
|  | bit 6 | unrecoverSpdFail(AC) | 143 | Lightning protection permanent fault - AC side | DSPM
|  | bit 7 |  | 144
Fault10 | byte 0 | bit 0 | USBFault | 145 | USB fault | ARM | Communication board
|  | bit 1 | WifiFault | 146 | WIFI fault | ARM
|  | bit 2 | BluetoothFault | 147 | Bluetooth fault | ARM
|  | bit 3 | RTCFault | 148 | RTC clock fault | ARM
|  | bit 4 | CommEEPROMFault | 149 | Communication board EEPROM error | ARM
|  | bit 5 | FlashFault | 150 | Communication board FLASH error | ARM
|  | bit 6 |  | 151
|  | bit 7 | SafetyVerFault | 152 | Safety regulation version error | ARM
| byte 1 | bit 0 | SciCommLose(DC) | 153 | SCI communication error (DC side) | ARM
|  | bit 1 | SciCommLose(AC) | 154 | SCI communication error (AC side) | ARM
|  | bit 2 | SciCommLose(Fuse) | 155 | SCI communication error (convergence board side) | ARM
|  | bit 3 | SoftVerError | 156 | Software version inconsistency | ARM
|  | bit 4 | BMS1CommunicatonFault | 157 | Lithium battery 1 communication error | ARM
|  | bit 5 | BMS2CommunicatonFault | 158 | Li-ion battery 2 communication error
|  | bit 6 | BMS3CommunicatonFault | 159 | Lithium battery 3 communication error
|  | bit 7 | BMS4CommunicatonFault | 160 | Lithium battery 4 communication failure
Fault11 | byte 0 | bit 0 | ForceShutdown | 161 | Forced shutdown | ARM | Communication board shutdown, load reduction
|  | bit 1 | RemoteShutdown | 162 | Remote shutdown | ARM
|  | bit 2 | Drms0Shutdown | 163 | Drms0 shutdown | ARM
|  | bit 3 |  | 164
|  | bit 4 | RemoteDerating | 165 | Remote down load | ARM
|  | bit 5 | LogicInterfaceDerating | 166 | Logic interface down load | ARM
|  | bit 6 | AlarmAntiRefluxing | 167 | Anti-Reverse Flow Downgrade | ARM
|  | bit 7 |  | 168
| byte 1 | bit 0 | FanFault1 | 169 | Fan 1 failure | ARM | Peripheral Components
|  | bit 1 | FanFault2 | 170 | Fan 2 failure | ARM
|  | bit 2 | FanFault3 | 171 | Fan 3 failure | ARM
|  | bit 3 | FanFault4 | 172 | Fan 4 failure | ARM
|  | bit 4 | FanFault5 | 173 | Fan 5 failure | ARM
|  | bit 5 | FanFault6 | 174 | Fan 6 failure | ARM
|  | bit 6 | FanFault7 | 175 | Fan 7 fault | ARM
|  | bit 7 | MeterCommLose | 176 | Meter communication failure | ARM
Fault12 | byte 0 | bit 0 | BMS OVP | 177 | BMS over-voltage alarm | BMS | BMS
|  | bit 1 | BMS UVP | 178 | BMS undervoltage alarm | BMS
|  | bit 2 | BMS OTP | 179 | BMS high temperature alarm | BMS
|  | bit 3 | BMS UTP | 180 | BMS low temperature alarm | BMS
|  | bit 4 | BMS OCP | 181 | BMS charge/discharge overload alarm | BMS
|  | bit 5 | BMS Short | 182 | BMS short circuit alarm | BMS
|  | bit 6 | BMS VerFault | 183 | BMS version inconsistency | ARM
|  | bit 7 | BMS CAN VerFault | 184 | BMS CAN version inconsistency | ARM
| byte 1 | bit 0 | BMS CAN VerLow | 185 | BMS CAN version is too low | ARM
|  | bit 1 |  | 186
|  | bit 2 |  | 187
|  | bit 3 |  | 188
|  | bit 4 | AFCICommLose | 189 | Arc device communication failure | ARM
|  | bit 5 | DCArcingAlarmFault | 190 | DC arc alarm fault | ARM
|  | bit 6 |  | 191
|  | bit 7 |  | 192
Fault13 | byte 0 | bit 0 | StringFuse_Fault0 | 193 | String fuse open circuit alarm | FUSE | Fuse
|  | bit 1 | StringFuse_Fault1 | 194 | String fuse open circuit alarm | FUSE
|  | bit 2 | StringFuse_Fault2 | 195 | String fuse open circuit alarm | FUSE
|  | bit 3 | StringFuse_Fault3 | 196 | String fuse open circuit alarm | FUSE
|  | bit 4 | StringFuse_Fault4 | 197 | String fuse open circuit alarm | FUSE
|  | bit 5 | StringFuse_Fault5 | 198 | String fuse open circuit alarm | FUSE
|  | bit 6 | StringFuse_Fault6 | 199 | String fuse open circuit alarm | FUSE
|  | bit 7 | StringFuse_Fault7 | 200 | String fuse open circuit alarm | FUSE
| byte 1 | bit 0 | StringFuse_Fault8 | 201 | String fuse open circuit alarm | FUSE
|  | bit 1 | StringFuse_Fault9 | 202 | String fuse open circuit alarm | FUSE
|  | bit 2 | StringFuse_Fault10 | 203 | String fuse open circuit alarm | FUSE
|  | bit 3 | StringFuse_Fault11 | 204 | String fuse open circuit alarm | FUSE
|  | bit 4 | StringFuse_Fault12 | 205 | String fuse open circuit alarm | FUSE
|  | bit 5 | StringFuse_Fault13 | 206 | String fuse open circuit alarm | FUSE
|  | bit 6 | StringFuse_Fault14 | 207 | String fuse open circuit alarm | FUSE
|  | bit 7 | StringFuse_Fault15 | 208 | String fuse open circuit alarm | FUSE
Fault14 | byte 0 | bit 0 | StringFuse_Fault16 | 209 | String fuse open circuit alarm | FUSE
|  | bit 1 | StringFuse_Fault17 | 210 | String fuse open circuit alarm | FUSE
|  | bit 2 | StringFuse_Fault18 | 211 | String fuse open circuit alarm | FUSE
|  | bit 3 | StringFuse_Fault19 | 212 | String fuse open circuit alarm | FUSE
|  | bit 4 | StringFuse_Fault20 | 213 | String fuse open circuit alarm | FUSE
|  | bit 5 | StringFuse_Fault21 | 214 | String fuse open circuit alarm | FUSE
|  | bit 6 | StringFuse_Fault22 | 215 | String fuse open circuit alarm | FUSE
|  | bit 7 | StringFuse_Fault23 | 216 | String fuse open circuit alarm | FUSE
| byte 1 | bit 0 | StringFuse_Fault24 | 217 | String fuse open circuit alarm | FUSE
|  | bit 1 | StringFuse_Fault25 | 218 | String fuse open circuit alarm | FUSE
|  | bit 2 | StringFuse_Fault26 | 219 | String fuse open circuit alarm | FUSE
|  | bit 3 | StringFuse_Fault27 | 220 | String fuse open circuit alarm | FUSE
|  | bit 4 | StringFuse_Fault28 | 221 | String fuse open circuit alarm | FUSE
|  | bit 5 | StringFuse_Fault29 | 222 | String fuse open circuit alarm | FUSE
|  | bit 6 | StringFuse_Fault30 | 223 | String fuse open circuit alarm | FUSE
|  | bit 7 | StringFuse_Fault31 | 224 | String fuse open circuit alarm | FUSE
Fault15 | byte 0 | bit 0 | InputFuse_Fault0 | 225 | Battery input fuse open circuit alarm | FUSE
|  | bit 1 | InputFuse_Fault1 | 226 | Battery input fuse open circuit alarm | FUSE
|  | bit 2 | InputFuse_Fault2 | 227 | Battery input fuse open circuit alarm | FUSE
|  | bit 3 | InputFuse_Fault3 | 228 | Battery input fuse open circuit alarm | FUSE
|  | bit 4 | InputFuse_Fault4 | 229 | Battery input fuse open circuit alarm | FUSE
|  | bit 5 | InputFuse_Fault5 | 230 | Battery input fuse open circuit alarm | FUSE
|  | bit 6 | InputFuse_Fault6 | 231 | Battery input fuse open circuit alarm | FUSE
|  | bit 7 | InputFuse_Fault7 | 232 | Battery input fuse open circuit alarm | FUSE
| byte 1 | bit 0 | InputFuse_Fault8 | 233 | Battery input fuse open circuit alarm | FUSE
|  | bit 1 | InputFuse_Fault9 | 234 | Battery input fuse open circuit alarm | FUSE
|  | bit 2 | InputFuse_Fault10 | 235 | Battery input fuse open circuit alarm | FUSE
|  | bit 3 | InputFuse_Fault11 | 236 | Battery input fuse open circuit alarm | FUSE
|  | bit 4 | InputFuse_Fault12 | 237 | Battery input fuse open circuit alarm | FUSE
|  | bit 5 | InputFuse_Fault13 | 238 | Battery input fuse open circuit alarm | FUSE
|  | bit 6 | InputFuse_Fault14 | 239 | Battery input fuse open circuit alarm | FUSE
|  | bit 7 | InputFuse_Fault15 | 240 | Battery input fuse open circuit alarm | FUSE
Fault16 | byte 0 | bit 0 | CombinerOverVoltageGroup1 | 241 |  |  | 汇流
|  | bit 1 | CombinerOverVoltageGroup2 | 242
|  | bit 2 | CombinerOverVoltageGroup3 | 243
|  | bit 3 | CombinerOverVoltageGroup4 | 244
|  | bit 4 | CombinerOverVoltageGroup5 | 245
|  | bit 5 | CombinerOverVoltageGroup6 | 246
|  | bit 6 | CombinerOverVoltageGroup7 | 247
|  | bit 7 | CombinerOverVoltageGroup8 | 248
| byte 1 | bit 0 | CombinerOverVoltageGroup9 | 249
|  | bit 1 | CombinerOverVoltageGroup10 | 250
|  | bit 2 | CombinerOverVoltageGroup11 | 251
|  | bit 3 | CombinerOverVoltageGroup12 | 252
|  | bit 4 | CombinerOverVoltageGroup13 | 253
|  | bit 5 | CombinerOverVoltageGroup14 | 254
|  | bit 6 | CombinerOverVoltageGroup15 | 255
|  | bit 7 | CombinerOverVoltageGroup16 | 256
Fault17 | byte 0 | bit 0 | CombinerUnderVoltageGroup1 | 257 |  |  | 汇流
|  | bit 1 | CombinerUnderVoltageGroup2 | 258
|  | bit 2 | CombinerUnderVoltageGroup3 | 259
|  | bit 3 | CombinerUnderVoltageGroup4 | 260
|  | bit 4 | CombinerUnderVoltageGroup5 | 261
|  | bit 5 | CombinerUnderVoltageGroup6 | 262
|  | bit 6 | CombinerUnderVoltageGroup7 | 263
|  | bit 7 | CombinerUnderVoltageGroup8 | 264
| byte 1 | bit 0 | CombinerUnderVoltageGroup9 | 265
|  | bit 1 | CombinerUnderVoltageGroup10 | 266
|  | bit 2 | CombinerUnderVoltageGroup11 | 267
|  | bit 3 | CombinerUnderVoltageGroup12 | 268
|  | bit 4 | CombinerUnderVoltageGroup13 | 269
|  | bit 5 | CombinerUnderVoltageGroup14 | 270
|  | bit 6 | CombinerUnderVoltageGroup15 | 271
|  | bit 7 | CombinerUnderVoltageGroup16 | 272
Fault18 | byte 0 | bit 0 | CombinerOverCurrent1 | 273 |  |  | 汇流
|  | bit 1 | CombinerOverCurrent2 | 274
|  | bit 2 | CombinerOverCurrent3 | 275
|  | bit 3 | CombinerOverCurrent4 | 276
|  | bit 4 | CombinerOverCurrent5 | 277
|  | bit 5 | CombinerOverCurrent6 | 278
|  | bit 6 | CombinerOverCurrent7 | 279
|  | bit 7 | CombinerOverCurrent8 | 280
| byte 1 | bit 0 | CombinerOverCurrent9 | 281
|  | bit 1 | CombinerOverCurrent10 | 282
|  | bit 2 | CombinerOverCurrent11 | 283
|  | bit 3 | CombinerOverCurrent12 | 284
|  | bit 4 | CombinerOverCurrent13 | 285
|  | bit 5 | CombinerOverCurrent14 | 286
|  | bit 6 | CombinerOverCurrent15 | 287
|  | bit 7 | CombinerOverCurrent16 | 288
Fault19 | byte 0 | bit 0 | CombinerOverCurrent17 | 289 |  |  | 汇流
|  | bit 1 | CombinerOverCurrent18 | 290
|  | bit 2 | CombinerOverCurrent19 | 291
|  | bit 3 | CombinerOverCurrent20 | 292
|  | bit 4 | CombinerOverCurrent21 | 293
|  | bit 5 | CombinerOverCurrent22 | 294
|  | bit 6 | CombinerOverCurrent23 | 295
|  | bit 7 | CombinerOverCurrent24 | 296
| byte 1 | bit 0 | CombinerOverCurrent25 | 297
|  | bit 1 | CombinerOverCurrent26 | 298
|  | bit 2 | CombinerOverCurrent27 | 299
|  | bit 3 | CombinerOverCurrent28 | 300
|  | bit 4 | CombinerOverCurrent29 | 301
|  | bit 5 | CombinerOverCurrent30 | 302
|  | bit 6 | CombinerOverCurrent31 | 303
|  | bit 7 | CombinerOverCurrent32 | 304
Fault20 | byte 0 | bit 0 |  | 305 |  |  | 汇流
|  | bit 1 |  | 306
|  | bit 2 |  | 307
|  | bit 3 |  | 308
|  | bit 4 |  | 309
|  | bit 5 |  | 310
|  | bit 6 |  | 311
|  | bit 7 |  | 312
| byte 1 | bit 0 |  | 313
|  | bit 1 |  | 314
|  | bit 2 |  | 315
|  | bit 3 |  | 316
|  | bit 4 |  | 317
|  | bit 5 |  | 318
|  | bit 6 |  | 319
|  | bit 7 |  | 320
Fault21 | byte 0 | bit 0 |  | 321 |  |  | 汇流
|  | bit 1 |  | 322
|  | bit 2 |  | 323
|  | bit 3 |  | 324
|  | bit 4 |  | 325
|  | bit 5 |  | 326
|  | bit 6 |  | 327
|  | bit 7 |  | 328
| byte 1 | bit 0 |  | 329
|  | bit 1 |  | 330
|  | bit 2 |  | 331
|  | bit 3 |  | 332
|  | bit 4 |  | 333
|  | bit 5 |  | 334
|  | bit 6 |  | 335
|  | bit 7 |  | 336
Fault22 | byte 0 | bit 0 | CombinerRefluxFault1 | 337 |  |  | 汇流
|  | bit 1 | CombinerRefluxFault2 | 338
|  | bit 2 | CombinerRefluxFault3 | 339
|  | bit 3 | CombinerRefluxFault4 | 340
|  | bit 4 | CombinerRefluxFault5 | 341
|  | bit 5 | CombinerRefluxFault6 | 342
|  | bit 6 | CombinerRefluxFault7 | 343
|  | bit 7 | CombinerRefluxFault8 | 344
| byte 1 | bit 0 | CombinerRefluxFault9 | 345
|  | bit 1 | CombinerRefluxFault10 | 346
|  | bit 2 | CombinerRefluxFault11 | 347
|  | bit 3 | CombinerRefluxFault12 | 348
|  | bit 4 | CombinerRefluxFault13 | 349
|  | bit 5 | CombinerRefluxFault14 | 350
|  | bit 6 | CombinerRefluxFault15 | 351
|  | bit 7 | CombinerRefluxFault16 | 352
Fault23 | byte 0 | bit 0 | CombinerRefluxFault17 | 353 |  |  | 汇流
|  | bit 1 | CombinerRefluxFault18 | 354
|  | bit 2 | CombinerRefluxFault19 | 355
|  | bit 3 | CombinerRefluxFault20 | 356
|  | bit 4 | CombinerRefluxFault21 | 357
|  | bit 5 | CombinerRefluxFault22 | 358
|  | bit 6 | CombinerRefluxFault23 | 359
|  | bit 7 | CombinerRefluxFault24 | 360
| byte 1 | bit 0 | CombinerRefluxFault25 | 361
|  | bit 1 | CombinerRefluxFault26 | 362
|  | bit 2 | CombinerRefluxFault27 | 363
|  | bit 3 | CombinerRefluxFault28 | 364
|  | bit 4 | CombinerRefluxFault29 | 365
|  | bit 5 | CombinerRefluxFault30 | 366
|  | bit 6 | CombinerRefluxFault31 | 367
|  | bit 7 | CombinerRefluxFault32 | 368
Fault24 | byte 0 | bit 0 |  | 369 |  |  | 汇流
|  | bit 1 |  | 370
|  | bit 2 |  | 371
|  | bit 3 |  | 372
|  | bit 4 |  | 373
|  | bit 5 |  | 374
|  | bit 6 |  | 375
|  | bit 7 |  | 376
| byte 1 | bit 0 |  | 377
|  | bit 1 |  | 378
|  | bit 2 |  | 379
|  | bit 3 |  | 380
|  | bit 4 |  | 381
|  | bit 5 |  | 382
|  | bit 6 |  | 383
|  | bit 7 |  | 384
Fault25 | byte 0 | bit 0 |  | 385 |  |  | 汇流
|  | bit 1 |  | 386
|  | bit 2 |  | 387
|  | bit 3 |  | 388
|  | bit 4 |  | 389
|  | bit 5 |  | 390
|  | bit 6 |  | 391
|  | bit 7 |  | 392
| byte 1 | bit 0 |  | 393
|  | bit 1 |  | 394
|  | bit 2 |  | 395
|  | bit 3 |  | 396
|  | bit 4 |  | 397
|  | bit 5 |  | 398
|  | bit 6 |  | 399
|  | bit 7 |  | 400
Fault26 | byte 0 | bit 0 | AFCI0 | 401 | Arc fault |  | AFCI
|  | bit 1 | AFCI1 | 402 | Arc fault
|  | bit 2 | AFCI2 | 403 | Arc fault
|  | bit 3 | AFCI3 | 404 | Arc fault
|  | bit 4 | AFCI4 | 405 | Arc fault
|  | bit 5 | AFCI5 | 406 | Arc fault
|  | bit 6 | AFCI6 | 407 | Arc fault
|  | bit 7 | AFCI7 | 408 | Arc fault
| byte 1 | bit 0 | AFCI8 | 409 | Arc fault
|  | bit 1 | AFCI9 | 410 | Arc fault
|  | bit 2 | AFCI10 | 411 | Arc fault
|  | bit 3 | AFCI11 | 412 | Arc fault
|  | bit 4 | AFCI12 | 413 | Arc fault
|  | bit 5 | AFCI13 | 414 | Arc fault
|  | bit 6 | AFCI14 | 415 | Arc fault
|  | bit 7 | AFCI15 | 416 | Arc fault
Fault27 | byte 0 | bit 0 | AFCI16 | 417 | Arc fault |  | AFCI
|  | bit 1 | AFCI17 | 418 | Arc fault
|  | bit 2 | AFCI18 | 419 | Arc fault
|  | bit 3 | AFCI19 | 420 | Arc fault
|  | bit 4 | AFCI20 | 421 | Arc fault
|  | bit 5 | AFCI21 | 422 | Arc fault
|  | bit 6 | AFCI22 | 423 | Arc fault
|  | bit 7 | AFCI23 | 424 | Arc fault
| byte 1 | bit 0 | AFCI24 | 425 | Arc fault
|  | bit 1 | AFCI25 | 426 | Arc fault
|  | bit 2 | AFCI26 | 427 | Arc fault
|  | bit 3 | AFCI27 | 428 | Arc fault
|  | bit 4 | AFCI28 | 429 | Arc fault
|  | bit 5 | AFCI29 | 430 | Arc fault
|  | bit 6 | AFCI30 | 431 | Arc fault
|  | bit 7 | AFCI31 | 432 | Arc fault

## Changelog
Change History
Version | Revisionist | Date | Reason for change and content Change and Reason
V1.0 | Chan Kin Chung | 2019-12-05 | New proposed
V1.1 | Chan Kin Chung | 2020-09-02 | New register address, fault ID
V1.2 | Chan Kin Chung | 2020-12-02 | New register address, fault ID, fix some register property errors
V1.3 | Chan Kin Chung | 2021-08-02 | Add PID configuration parameters and control parameters
V1.4 | Liu Yonglai | 2021-08-11 | add configuration parameters for PLC and BLE, add remote reset command add extend the number of bits of serial number for production, the Add peripheral correspondence table Modified the configuration address of PID Added PLC heartbeat fault
V1.5 | Chan Kin Chung | 2021-08-31 | Fixed reactive configuration type issue, the group string open circuit alarm name change, the Protocol version number added